## Owerview_data
GOLD_E_F_EXOline_250905
EXOline 485/TCP
GOLD RX/PX/CX/SD, GENERATION E/F
Applicable to program version 1.10 and newer versions
Overview
The GOLD air handling unit will be an EXOline slave, and will be connected to the network with two-wire RS485. The most common settings are baudrate 9600, parity odd and stop bits 1. Can also be connected via TCP.
Slave address (PLA, ELA)
The slave address of an EXOline slave consists of two bytes PLA and ELA.
EXOline Data formats
EXOline data types that will be used:
EXOline Type |  | Description
Logical var. |  | 1 bit Discrete value
Index var. |  | One byte unsigned value
Real var. |  | Floating point value
Supported EXOline commands.
The GOLD air handling unit supports these EXOline commands.
Opc | Hex | Dec | Interpretation |  | Data | Answer
SLV | 01 | 1 | Set logical var. |  | DLn Cell Value | Ok!
SLP | 2F | 47 | Set logic segment var. |  | DLn Seg Offs Value | Ok!
SXV | 02 | 2 | Set index var. |  | DLn Cell Value | Ok!
SXP | B0 | 176 | Set index segment var. |  | DLn Seg Offs Value | Ok!
SRV | 04 | 4 | Set real var. |  | DLn Cell Value (4) | Ok!
SRP | 32 | 50 | Set real segment var. |  | DLn Seg Offs Value (4) | Ok!
RLV | 86 | 134 | Read logical var. |  | DLn Cell | Value
RLP | B3 | 179 | Read logic segment var. |  | DLn Seg Offset | Value
RXV | 07 | 7 | Read index var. |  | DLn Cell | Value
RXP | 34 | 52 | Read index segment var. |  | DLn Seg Offset | Value
RRV | 89 | 137 | Read real var. |  | DLn Cell | Value (4)
RRP | B6 | 182 | Read real segment var. |  | DLn Seg Offset | Value (4)
READV | 10 | 16 | Read Vpac page. |  | DLnDPn | Data (n)
Return error codes
The following error codes will be used.
Error code | Error |  |  | Fault that can occur
01h | Wrong data type |  |  | Accessing Cell with wrong data type.
07h | The DPac does not exist. |  |  | Accessing a Dpac that’s not used.
19h | Illegal parameter value |  |  | Try to write to an ”Read only” or value is out of range.
25h | Illegal cell number |  |  | Accessing Cell number that is not first Cell of a real var. Accessing Cell number that is not used.
26h | Illegal command |  |  | Command not supported
27h | Illegal message length |  |  | Wrong message length for command.
04h | Illegal DPac load number
05h | The DPac (or DPac segment) does not exist
GOLD
1
2
3
A
B
GND
EXOline
B
A
N

## Overview parameters
GOLD_E_F_EXOline_250905
Operation level | Vp3,592 | EA AHU filter pressure level |  | Vp2,29 |  | EA Temperature |  | Vp2,66
Communication operation level | Vp6,793 | EA AHU filter pressure alarm limit |  | Vp2,30 |  | EA/Room temperature set point |  | Vp5,135
Operation active | Vp4,1 |  |  |  |  | SA min temp set point |  | Vp5,136
Low speed operation active | Vp4,3 |  |  |  |  | SA max temp set point |  | Vp5,137
High speed operation active | Vp4,4 |  | EA Duct pressure |  | Vp2,10
Damper operation active | Vp4,2 |  | EA low speed pressure set point |  | Vp5,20
Triggered alarm #1 | Vp2,604 |  | EA high speed pressure set point |  | Vp5,22 | SA Duct pressure |  | Vp2,8
A-alarm active | Vp4,13 |  |  |  |  | SA low speed pressure set point |  | Vp5,19
B-alarm active | Vp4,14 |  |  |  |  | SA high speed pressure set point |  | Vp5,21
Alarm reset | Vp7,1
[6 empty] | SA Temperature |  | Vp2,64
EA Air flow | Vp2,6 |  |  |  |  | SA temperature set point |  | Vp5,132
EA Fan level | Vp2,38 |  |  |  |  | ERS 1 diff |  | Vp5,118
EA low speed air flow set point | Vp5,3
EA high speed air flow set point | Vp5,6
Outdoor temperature | Vp2,73
SA AHU filter pressure level | Vp2,27
SA AHU filter pressure alarm limit | Vp2,28
RX
Heat exchanger regulator level | Vp2,91
RHX operation level | Vp2,105
PX | [6 empty] | Cool regulator level | Vp2,101
PHX-2 Damper 2 output | Vp2,123 | [5 empty] | Cool output 1 | Vp4,43
PHX-2 Bypass output | Vp2,125 | [5 empty] | Cool output 2 | Vp4,44
PHX-2 Damper 1 output | Vp2,121
CX |  | SA Air flow |  | Vp2,4 | Reheat regulator level |  | Vp2,94
CHX-2 Valve output | Vp2,137 | SA Fan level |  | Vp2,37 | Re-heat output |  | Vp4,38
CHX-2 Pump output | Vp2,139 | SA low speed air flow set point |  | Vp5,3 | Re-heat anti frost temp/overheat input |  | Vp2,153
CHX-1 pump output | Vp4,27 | SA high speed air flow set point |  | Vp5,5

## Vpac 2 (RO)
GOLD_E_F_EXOline_250905
Real var. Vpac 2 (RO)
Index | Cell nbr | Name | Description | Min | Max | Unit | Default | Misc
AHU Air flow/duct pressure
1 | 0 | Component name | 25=Iqlogic | 0 | 999
2 | 3
3 | 6
Air flow regulation
4 | 9 | SA Air flow | Present supply air flow. | 0 | 20000 | l/s
5 | 12 | SA Air flow regulator | Present supply air flow regulator set point. | 0 | 20000 | l/s
6 | 15 | EA Air flow | Present extract air flow. | 0 | 20000 | l/s
7 | 18 | EA Air flow regulator | Present extract air flow regulator set point. | 0 | 20000 | l/s
Pressure regulation
8 | 21 | SA Duct pressure | Present supply air duct pressure. | 0.0 | 2000.0 | Pa
9 | 24 | SA Duct pressure regulator | Present supply air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
10 | 27 | EA Duct pressure | Present extract air duct pressure. | 0.0 | 2000.0 | Pa
11 | 30 | EA Duct pressure regulator | Present extract air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
Demand regulation
12 | 33 | Demand input level | Present input signal for demand regulation. | 0.00 | 100.00 | %
13 | 36 | Demand regulator | Present demand regulator set point. | 0.00 | 100.00 | %
Air flow pressure sensors
14 | 39 | SA Air flow pressure | Present air flow pressure in the supply air fan inlet. | 0.0 | 2000.0 | Pa
15 | 42 | EA Air flow pressure | Present air flow pressure in the extract air fan inlet. | 0.0 | 2000.0 | Pa
16 | 45
17 | 48
Demand regulation
18 | 51 | Demand CO2 regulator | Present demand CO2 regulator set point. | 0 | 10000 | ppm |  | 1.23
19 | 54 | Demand VOC regulator | Present demand VOC regulator set point. | 0 | 10000 | ppm |  | 1.23
20 | 57
21 | 60
22 | 63
Filters
23 | 66 | SA Pre-filter pressure level | Present supply air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
24 | 69 | SA Pre-filter pressure alarm limit | Present supply air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
25 | 72 | EA Pre-filter pressure level | Present extract air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
26 | 75 | EA Pre-filter pressure alarm limit | Present extract air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
27 | 78 | SA AHU filter pressure level | Present supply air filter pressure drop. | 0.0 | 2000.0 | Pa
28 | 81 | SA AHU filter pressure alarm limit | Present supply air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
29 | 84 | EA AHU filter pressure level | Present extract air filter pressure drop. | 0.0 | 2000.0 | Pa
30 | 87 | EA AHU filter pressure alarm limit | Present extract air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
31 | 90 | SA End-filter pressure level | Present supply air end-filter pressure drop. | 0.0 | 2000.0 | Pa
32 | 93 | SA End-filter pressure alarm limit | Present supply air end-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
33 | 96
34 | 99
35 | 102
36 | 105
Fans
37 | 108 | SA Fan level | Present fan speed level of the supply air fan. | 0.00 | 100.00 | %
38 | 111 | EA Fan level | Present fan speed level of the extract air fan. | 0.00 | 100.00 | %
39 | 114 | SA Fan speed | Present fan speed level of the supply air fan. | 0 | 4000 | rpm
40 | 117 | EA Fan speed | Present fan speed level of the extract air fan. | 0 | 4000 | rpm
41 | 120 | SA Voltage | Present voltage level of the supply air fan. | 0 | 500 | V
42 | 123 | EA Voltage | Present voltage level of the extract air fan. | 0 | 500 | V
43 | 126 | SA Fan current | Present current level of the supply air fans. Includes all supply air fans. | 0 | 32.700 | A
44 | 129 | EA Fan current | Present current level of the extract air fans. Includes all supply air fans. | 0 | 32.700 | A
45 | 132 | SA Fan power | Present power level of the supply air fans. Includes all supply air fans. | 0 | 45.000 | kW
46 | 135 | EA Fan power | Present power consumption level of the extract air fans. Includes all extract air fans. | 0 | 45.000 | kW
47 | 138 | SA Fan kWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | kWh
48 | 141 | EA Fan kWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | kWh
49 | 144 | SA Fan MWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | MWh
50 | 147 | EA Fan MWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | MWh
51 | 150 | SA Fan operation time | Total operation time of the supply air fan presented in days (24h). | 0..9999 | 9999 | days
52 | 153 | EA Fan operation time | Total operation time of the extract air fan presented in days (24h). | 0..9999 | 9999 | days
53 | 156
54 | 159
55 | 162 | SA Fan min air flow | Supply air AHU min air flow | 0 | 18000 | l/s
56 | 165 | EA Fan min air flow | Extract air AHU min air flow | 0 | 18000 | l/s
57 | 168 | SA Fan max air flow | Supply air AHU max air flow | 0 | 18000 | l/s
58 | 171 | EA Fan max air flow | Extract air AHU max air flow | 0 | 18000 | l/s
59 | 174
60 | 177
61 | 180
62 | 183
63 | 186 | SFP | Calculated SFP level. | 0.00 | 100.00 | kW/m3/s
AHU Temperature sensors
64 | 189 | SA Temperature | Present supply air temperature. | -55.00 | 125.00 | °C
65 | 192 | SA-D Temperature | Present supply air density temperature. | -55.00 | 125.00 | °C
66 | 195 | EA Temperature RX | Present extract air temperature in the unit (only AHU type RX). | -55.00 | 125.00 | °C
67 | 198 | EA-D Temperature | Present extract air density temperature. | -55.00 | 125.00 | °C
68 | 201 | EA Regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
69 | 204 | EA Temperature PX/CX | Present extract air temperature in the unit (only AHU type PX/CX). | -55.00 | 125.00 | °C |  | 1.13
70 | 207 | EA Temperature SD | Present extract air temperature in the unit (only AHU type SD). | -55.00 | 125.00 | °C |  | 1.13
71 | 210
72 | 213 | Outdoor temperature COOL DX | Present outdoor air temperature in the COOL DX unit. | -55.00 | 125.00 | °C |  | 1.13
73 | 216 | Outdoor temperature | Present outdoor air temperature in the unit. | -55.00 | 125.00 | °C
74 | 219 | Outdoor regulation temperature | Present outdoor air temperature used for regulation. | -55.00 | 125.00 | °C
75 | 222 | External outdoor temperature 1 | Present external outdoor temperature of sensor 1. | -55.00 | 125.00 | °C
76 | 225 | External outdoor temperature 2 | Present external outdoor temperature of sensor 2. | -55.00 | 125.00 | °C
77 | 228 | External outdoor temperature 3 | Present external outdoor temperature of sensor 3. | -55.00 | 125.00 | °C
78 | 231 | External outdoor temperature 4 | Present external outdoor temperature of sensor 4. | -55.00 | 125.00 | °C
79 | 234 | External outdoor temperature min/max/average | Present calculated min, max or average (depending of configuration) temperature of outd. sensor 1-4. | -55.00 | 125.00 | °C
80 | 237 | EA duct temperature | Present extract air duct air temperature. | -55.00 | 125.00 | °C |  | 1.12
81 | 240 | Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
82 | 243 | Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
83 | 246 | Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
84 | 249 | Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
85 | 252 | Room temperature min/max/average | Present calculated min, max or average (depending of configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
86 | 255
AHU Temperature regulation
87 | 258 | SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
88 | 261 | EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
89 | 264
90 | 267 | Cool exchanger regulator level | Present operation level of cool recovery. | 0.00 | 100.00 | % |  | 1.11
91 | 270 | Heat exchanger regulator level | Present operation level of the rotary heat exchanger. | 0.00 | 100.00 | %
92 | 273 | Extra regulation sequence 1 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | %
93 | 276 | Extra regulation sequence 1 heat output level |  | 0.00 | 100.00 | %
94 | 279 | Reheat regulator level | Present level of reheat. | 0.00 | 100.00 | %
95 | 282 | Reheat output level |  | 0.00 | 100.00 | %
96 | 285 | ReCO2 heat level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
97 | 288 | Down regulation level | Present level of fan down regulation. | 0.00 | 100.00 | %
98 | 291 | Heating boost level | Present level of heating boost. | 0.00 | 100.00 | %
99 | 294 | Extra regulation sequence 1 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | %
100 | 297 | Extra regulation sequence 1 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | %
101 | 300 | Cool regulator level | Present level of cooling. | 0.00 | 100.00 | %
102 | 303 | Cool output level | Present level of cooling. | 0.00 | 100.00 | %
103 | 306 | ReCO2 cool level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
104 | 309 | Cooling boost level | Present level of cooling boost. | 0.00 | 100.00 | %
AHU heat exchange
105 | 312 | RHX operation level | Present speed level of the rotary heat exchanger. | 0.00 | 100.00 | %
106 | 315 | RHX/PHX/CHX efficiency | Calculated level of the heat exchanger efficiency. | 0.00 | 100.00 | % |  | 1.23
107 | 318 | RHX defrost pressure level | Present pressure drop for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
108 | 321 | RHX defrost pressure alarm limit | Present pressure drop alarm limit for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
109 | 324 | RHX carry over control pressure level | Present pressure difference for the rotary heat exchangers purging sector. | 0.0 | 1000.0 | Pa
110 | 327
111 | 330 | RHX operation time | Total operation time of the rotary heat exchanger presented in days (24h). | 0 | 9999 | Days
112 | 333
113 | 336
114 | 339
115 | 342
116 | 345 | PHX-2/3 pressure drop level | Present pressure drop for the plate heat exchanger. | 0.0 | 2000.0 | Pa |  | 1.13
117 | 348 | PHX-1 Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | %
118 | 351 | PHX-1 Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | %
119 | 354 | PHX-1 Bypass temperature 1 | Present bypass temperature sensor 1 in plate heat exchanger. | -55.00 | 125.00 | °C
120 | 357 | PHX-1 Bypass temperature 2 | Present bypass temperature sensor 2 in plate heat exchanger. | -55.00 | 125.00 | °C
121 | 360 | PHX-2 Damper 1 output | Present level of plate heat exchanger damper 1 output. | 0.00 | 100.00 | % |  | 1.13
122 | 363 | PHX-2 Damper 1 input | Present level of plate heat exchanger damper 1 input. | 0.00 | 100.00 | % |  | 1.16
123 | 366 | PHX-2 Damper 2 output | Present level of plate heat exchanger damper 2 output. | 0.00 | 100.00 | % |  | 1.13
124 | 369 | PHX-2 Damper 2 input | Present level of plate heat exchanger damper 2 input. | 0.00 | 100.00 | % |  | 1.16
125 | 372 | PHX-2 Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | % |  | 1.13
126 | 375 | PHX-2 Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | % |  | 1.13
127 | 378 | CHX-1 Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | %
128 | 381 | CHX-1 Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | %
129 | 384 | CHX-1 Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C
130 | 387 | PHX/CHX operation time | Total operation time of the coil heat exchanger presented in days (24h). | 0 | 9999 | Days
131 | 390
132 | 393 | PHX-3 Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | % |  | 1.12
133 | 396 | PHX-3 Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | % |  | 1.12
134 | 399 | CHX-2 Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C |  | 1.18
135 | 402 | CHX-2 Extract coil pressure level | Present extract coil differiential pressure. | 0 | 1600 | mBar |  | 1.18
136 | 405 | PHX-1/2 /CHX Humidity level | Present level of air-humidity for calculation of bypass/valve limitation. | 0.00 | 100.00 | %
137 | 408 | CHX-2 Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | % |  | 1.18
138 | 411 | CHX-2 Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | % |  | 1.18
139 | 414 | CHX-2 Pump output | Present level of pump heat exchanger output | 0.00 | 100.00 | % |  | 1.18
AHU Coils
140 | 417
141 | 420 | Extra regulation sequence 1 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
142 | 423
143 | 426 | Extra regulation sequence 2 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 1.13
144 | 429 | Extra regulation sequence 1 temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
145 | 432 | Extra regulation sequence 2 temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
146 | 435 | Extra regulation sequence 1 input level |  | 0.00 | 100.00 | %
147 | 438 | Extra regulation sequence 1 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 9999 | Days
148 | 441 | Extra regulation sequence 1 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 9999 | Days
149 | 444 | Extra regulation sequence 2 input level |  | 0.00 | 100.00 | % |  | 1.13
150 | 447 | Extra regulation sequence 2 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 9999 | Days |  | 1.13
151 | 450 | Extra regulation sequence 2 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 9999 | Days |  | 1.13
152 | 453 | Re-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
153 | 456 | Re-heat anti frost temp/overheat input | Present anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
154 | 459
155 | 462
156 | 465
157 | 468
158 | 471 | Re-heat input level |  | 0.00 | 100.00 | %
159 | 474 | Re-heat operation time | Total operation time of re-heat presented in days (24h). | 0 | 9999 | Days
160 | 477
161 | 480
162 | 483
163 | 486 | Cool coil type | 0=None,1..8=N/A, 9..10=Water, 11..15=N/A | 0 | 15
164 | 489 | Cool water temperature | Present cool water temperature for water cool coil. | -55.00 | 125.00 | °C
165 | 492
166 | 495
167 | 498
168 | 501 | Cool input level |  | 0.00 | 100.00 | %
169 | 504 | Cool operation time | Total operation time of cool presented in days (24h). | 0 | 9999 | Days
170 | 507
171 | 510
172 | 513
173 | 516
Xzone temperature sensors
174 | 519 | Xzone SA temperature | Present supply air temperature. | -55.00 | 125.00 | °C
175 | 522 | Xzone EA temperature | Present extract air temperature in the unit. | -55.00 | 125.00 | °C
176 | 525 | Xzone EA regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
177 | 528 | Xzone Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
178 | 531 | Xzone Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
179 | 534 | Xzone Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
180 | 537 | Xzone Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
181 | 540 | Xzone Room temperature min/max/average | Present calculated min, max or average (depending on configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
182 | 543
183 | 546
184 | 549
185 | 552
Xzone Temperature regulation
186 | 555 | Xzone SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
187 | 558 | Xzone EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
188 | 561
189 | 564
190 | 567 | Xzone re-heat regulator level |  | 0.00 | 100.00 | %
191 | 570
192 | 573
193 | 576 | Xzone cool regulator level |  | 0.00 | 100.00 | %
194 | 579
195 | 582
196 | 585
197 | 588
Xzone coils
198 | 591
199 | 594 | Xzone heat, anti frost temp/overheat input | Present Xzone heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
200 | 597 | Xzone heat/cool temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
201 | 600
202 | 603
203 | 606 | Xzone heat, output level | Present level of Xzone heat output. | 0 | 100.00 | %
204 | 609 | Xzone heat, input level | Present Xzone heat input. | 0 | 100.00 | %
205 | 612 | Xzone heat, operation time | Total operation time of Xzone heat presented in days (24h). | 0 | 9999
206 | 615
207 | 618
208 | 621
209 | 624 | Xzone cool, coil type | 9..10=Water | 0 | 15
210 | 627 | Xzone cool, water temperature |  | -55.00 | 125.00 | °C
211 | 630 | Xzone cool temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
212 | 633
213 | 636
214 | 639 | Xzone cool, output level | Present level of Xzone cool. | 0 | 100.00 | %
215 | 642 | Xzone cool, input level | Present Xzone cool valve position. | 0 | 100.00 | %
216 | 645 | Xzone cool, operation time | Total operation time of Xzone cool presented in days (24h). | 0 | 9999
217 | 648
218 | 651
219 | 654
Pre-heat
220 | 657 | Pre-heat temperature | Present pre-heat temperature. | -55.00 | 125.00 | °C
221 | 660 | Pre-heat temp regulator set point | Present pre-heat temperature regulator set point. | -40.00 | 40.00 | °C
222 | 663 | Pre-heat temp regulator level
223 | 666
224 | 669 | Pre-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
225 | 672 | Pre-heat anti frost temp/overheat input | Present pre-heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
226 | 675
227 | 678
228 | 681 | Pre-heat output level | Present pre-heat output level. | 0.00 | 100.00 | %
229 | 684 | Pre-heat input level | Present pre-heat input level. | 0.00 | 100.00 | %
230 | 687 | Pre-heat operation time | Total operation time of pre-heat presented in days (24h). | 0 | 9999 | Days
231 | 690
232 | 693
ReCO2
233 | 696 | ReCO2 recirculation damper output | Present output signal to the recirculation damper. | 0.00 | 100.00 | %
234 | 699 | ReCO2 recirculation damper input | Present input signal from the recirculation damper. | 0.00 | 100.00 | %
235 | 702 | ReCO2 outdoor damper output | Present output signal to the outdoor air damper. | 0.00 | 100.00 | %
236 | 705 | ReCO2 outdoor damper input | Present input signal from the outdoor air damper. | 0.00 | 100.00 | %
237 | 708 | ReCO2 outdoor air flow | Present outdoor air flow level. | 0.0 | Vp2,57 | l/s
238 | 711 | ReCO2 outdoor air flow regulator set point | Present outdoor air flow regulator set point. | 0.0 | 2000.0 | Pa
239 | 714
240 | 717
241 | 720
242 | 723
243 | 726
Humidity
244 | 729 | SA humidity level | Present level of supply air humidity | 0.00 | 100.00 | %RH
245 | 732 | SA humidity temperature | Present temperature inside the supply air humidity sensor. | -40.00 | 123.00 | °C
246 | 735 | SA dew point | Calculated supply air dew point. | -40.00 | 40.00 | °C
247 | 738 | EA humidity level | Present level of extract air humidity. | 0.00 | 100.00 | %RH
248 | 741 | EA humidity temperature | Present temperature inside the extract air humidity sensor. | -40.00 | 123.00 | °C
249 | 744 | EA dew point | Calculated extract air dew point. | -40.00 | 40.00 | °C
250 | 747
251 | 750 | Dehumidifying SA dew point regulator set point | Present supply air dew point regulator point. | -40.00 | 40.00 | °C
252 | 753 | Dehumidifying output level | Present level of the dehumidifying output. | 0.00 | 100.00 | %
253 | 756
254 | 759 | Humidifying SA regulator set point |  | 0.00 | 100.00 | %RH
255 | 762 | Humidifying output level | Present level of the dehumidifying output. | 0.00 | 100.00 | %
256 | 765
257 | 768
258 | 771
259 | 774
260 | 777 | Exhaust air humidity | Present level of exhaust air humidity. | 0.00 | 100.00 | %RH |  | 1.23
261 | 780 | Exhaust air temperature | Present temperature inside the exhaust air humidity sensor. | -40.00 | 123.00 | °C |  | 1.23
262 | 783 | Outdoor air humidity | Present level of outdoor air humidity. | 0.00 | 100.00 | %RH |  | 2.37
263 | 786 | Outdoor air temperature | Present temperature inside the outdoor air humidity sensor. | -40.00 | 123.00 | °C |  | 2.37
264 | 789 | Room air humidity | Present level of room air humidity. | 0.00 | 100.00 | %RH |  | 2.37
265 | 792 | Room air temperature | Present temperature inside the room air humidity sensor. | -40.00 | 123.00 | °C |  | 2.37
VOC
266 | 795 | VOC level | Present level of VOC | 450 | 10000 | ppm
267 | 798 | CO2 level | Present level of CO2 | 0 | 10000 | ppm |  | 1.23
268 | 801
269 | 804
270 | 807
COOL DX
271 | 810 | COOL DX, unit power size |  | 0 | 15
272 | 813
273 | 816
274 | 819 | COOL DX, compressor 1 low pressure level |  | 0 | 34.50 | Bar
275 | 822 | COOL DX, compressor 1 high pressure level |  | 0 | 45.00 | Bar
276 | 825 | COOL DX, compressor 2 low pressure level |  | 0 | 34.50 | Bar
277 | 828 | COOL DX, compressor 2 high pressure level |  | 0 | 45.00 | Bar
278 | 831
279 | 834
Exhaust heat
280 | 837
281 | 840 | Exhaust heat temperature | Present exhaust heat temperature | -55.00 | 125.00 | °C |  | 2.43
282 | 843 | Exhaust heat temp regulator set point | Present exhaust heat temp regulator set point | -40.00 | 40.00 | °C |  | 2.43
283 | 846 | Exhaust heat temp regulator level | [5 empty] | 2.43
284 | 849
285 | 852 | Exhaust heat anti frost temp/overheat input | Present exhaust heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 2.43
286 | 855 | Exhaust heat output level | Present exhaust heat output level. | 0.00 | 100.00 | % |  | 2.43
287 | 858 | Exhaust heat input level | Present exhaust heat input level. | 0.00 | 100.00 | % |  | 2.43
288 | 861 | Exhaust heat operation time | Total operation time of exhaust heat presented in days (24h). | 0 | 30000 | Days |  | 2.43
SMART Link
289 | 864 | SMART Link, WB outlet water 1 |  | -40.0 | 176.0 | °C
290 | 867 | SMART Link, WB outlet water 2 |  | -40.0 | 176.0 | °C
291 | 870 | SMART Link, WB outlet water 3 |  | -40.0 | 176.0 | °C
292 | 873 | SMART Link, WB outlet water 4 |  | -40.0 | 176.0 | °C
293 | 876 | SMART Link, WB outlet water average |  | -40.0 | 176.0 | °C
294 | 879 | SMART Link, WB reference water
295 | 882
296 | 885
297 | 888 | SMART Link WB, heated water set point |  | -40.0 | 176.0 | °C
298 | 891 | SMART Link WB, chilled water set point |  | -40.0 | 176.0 | °C
299 | 894 | SMART Link WB, Min heated water set point |  | -40.0 | 176.0 | °C
300 | 897 | SMART Link WB, Max heated water set point |  | -40.0 | 176.0 | °C
301 | 900 | SMART Link WB, Min chilled water set point |  | -40.0 | 176.0 | °C
302 | 903 | SMART Link WB, Max chilled water set point |  | -40.0 | 176.0 | °C
303 | 906
304 | 909
305 | 912
306 | 915
307 | 918
308 | 921
309 | 924
310 | 927
311 | 930
312 | 933
313 | 936
314 | 939
315 | 942
316 | 945
317 | 948
318 | 951
319 | 954
320 | 957
321 | 960
322 | 963
323 | 966
324 | 969
325 | 972
326 | 975
327 | 978 | SMART Link, DX unit 1 power level set point |  | 0 | 100.00 | %
328 | 981 | SMART Link, DX unit 1 power level |  | 0 | 100.00 | %
329 | 984 | SMART Link, DX unit 1 operation time |  | 0 | 9999
330 | 987
331 | 990
332 | 993
333 | 996
334 | 999
335 | 1002
336 | 1005
337 | 1008
338 | 1011 | SMART Link, DX unit 2 power level set point |  | 0 | 100.00 | %
339 | 1014 | SMART Link, DX unit 2 power level |  | 0 | 100.00 | %
340 | 1017 | SMART Link, DX unit 2 operation time |  | 0 | 9999
341 | 1020
342 | 1023
343 | 1026
344 | 1029
345 | 1032
346 | 1035
347 | 1038
348 | 1041
349 | 1044 | SMART Link, DX unit 3 power level set point |  | 0 | 100.00 | %
350 | 1047 | SMART Link, DX unit 3 power level |  | 0 | 100.00 | %
351 | 1050 | SMART Link, DX unit 3 operation time |  | 0 | 9999
352 | 1053
353 | 1056
354 | 1059
355 | 1062
356 | 1065
357 | 1068
358 | 1071
359 | 1074
360 | 1077 | SMART Link, DX unit 4 power level set point |  | 0 | 100.00 | %
361 | 1080 | SMART Link, DX unit 4 power level |  | 0 | 100.00 | %
362 | 1083 | SMART Link, DX unit 4 operation time |  | 0 | 9999
363 | 1086
364 | 1089
365 | 1092
366 | 1095
367 | 1098
368 | 1101
369 | 1104
370 | 1107
371 | 1110
372 | 1113
373 | 1116
AYC
374 | 1119 | AYC Heat, heated water | Present heat temperature. | -55.00 | 125.00 | °C
375 | 1122 | AYC Heat, heated water set point | Present heat temperature regulator set point. | 0 | 100.00 | °C
376 | 1125 | AYC Heat, valve output | Present level of the heat valve output. | 0 | 100.00 | %
377 | 1128 | AYC Heat, valve input | Present level of the heat valve input. | 0 | 100.00 | %
378 | 1131 | AYC Heat, operation time | Total operation time of AYC heat presented in days (24h). | 0 | 9999
379 | 1134 | AYC Heated water heat demand |  | 0 | 100.00 | %
380 | 1137
381 | 1140
382 | 1143
383 | 1146
384 | 1149
385 | 1152
386 | 1155
387 | 1158 | AYC Cool, chilled water | Present cool temperature. | -55.00 | 125.00 | °C
388 | 1161 | AYC Cool, chilled water set point | Present cool temperature regulator set point. | 0 | 100.00 | °C
389 | 1164 | AYC Cool, valve output | Present cool of the heat valve output. | 0 | 100.00 | %
390 | 1167 | AYC Cool, valve input | Present cool of the heat valve input. | 0 | 100.00 | %
391 | 1170 | AYC Cool, operation time | Total operation time of AYC cool presented in days (24h). | 0 | 9999
392 | 1173 | AYC Chilled water cool demand |  | 0 | 100.00 | %
393 | 1176
394 | 1179
395 | 1182
396 | 1185
397 | 1188
398 | 1191
399 | 1194
MIRU Control
400 | 1197 | MIRU Control 1 Min air flow | Min possible air flow setting |  |  | l/s
401 | 1200 | MIRU Control 1 Max air flow | Max possible air flow setting |  |  | l/s
402 | 1203 | MIRU Control 1 Air flow | Present air flow. |  |  | l/s
403 | 1206 | MIRU Control 1 Air flow set point | Present air flow regulator set point. |  |  | l/s
404 | 1209 | MIRU Control 1 Pressure | Present duct pressure. | 0 | 750 | Pa
405 | 1212 | MIRU Control 1 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
406 | 1215 | MIRU Control 1 External temperature | Present external temperature. | -55.00 | 95.00 | °C
407 | 1218 | MIRU Control 1 Operation time | Present operation time, present in days (24h). | 0 | 9999
408 | 1221 | MIRU Control 1 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
409 | 1224 | MIRU Control 1 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
410 | 1227 | MIRU Control 1 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
411 | 1230 | MIRU Control 1 kWh | kWh value. | 0 | 9999 | kWh
412 | 1233 | MIRU Control 1 MWh | MWh value. | 0 | 32000 | MWh
413 | 1236
414 | 1239
415 | 1242
416 | 1245
417 | 1248 | MIRU Control 2 Min air flow | Min possible air flow setting |  |  | l/s
418 | 1251 | MIRU Control 2 Max air flow | Max possible air flow setting |  |  | l/s
419 | 1254 | MIRU Control 2 Air flow | Present air flow. |  |  | l/s
420 | 1257 | MIRU Control 2 Air flow set point | Present air flow regulator set point. |  |  | l/s
421 | 1260 | MIRU Control 2 Pressure | Present duct pressure. | 0 | 750 | Pa
422 | 1263 | MIRU Control 2 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
423 | 1266 | MIRU Control 2 External temperature | Present external temperature. | -55.00 | 95.00 | °C
424 | 1269 | MIRU Control 2 Operation time | Present operation time, present in days (24h). | 0 | 9999
425 | 1272 | MIRU Control 2 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
426 | 1275 | MIRU Control 2 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
427 | 1278 | MIRU Control 2 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
428 | 1281 | MIRU Control 2 kWh | kWh value. | 0 | 9999 | kWh
429 | 1284 | MIRU Control 2 MWh | MWh value. | 0 | 32000 | MWh
430 | 1287
431 | 1290
432 | 1293
433 | 1296
434 | 1299 | MIRU Control 3 Min air flow | Min possible air flow setting |  |  | l/s
435 | 1302 | MIRU Control 3 Max air flow | Max possible air flow setting |  |  | l/s
436 | 1305 | MIRU Control 3 Air flow | Present air flow. |  |  | l/s
437 | 1308 | MIRU Control 3 Air flow set point | Present air flow regulator set point. |  |  | l/s
438 | 1311 | MIRU Control 3 Pressure | Present duct pressure. | 0 | 750 | Pa
439 | 1314 | MIRU Control 3 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
440 | 1317 | MIRU Control 3 External temperature | Present external temperature. | -55.00 | 95.00 | °C
441 | 1320 | MIRU Control 3 Operation time | Present operation time, present in days (24h). | 0 | 9999
442 | 1323 | MIRU Control 3 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
443 | 1326 | MIRU Control 3 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
444 | 1329 | MIRU Control 3 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
445 | 1332 | MIRU Control 3 kWh | kWh value. | 0 | 9999 | kWh
446 | 1335 | MIRU Control 3 MWh | MWh value. | 0 | 32000 | MWh
447 | 1338
448 | 1341
449 | 1344
450 | 1347
451 | 1350 | MIRU Control 4 Min air flow | Min possible air flow setting |  |  | l/s
452 | 1353 | MIRU Control 4 Max air flow | Max possible air flow setting |  |  | l/s
453 | 1356 | MIRU Control 4 Air flow | Present air flow. |  |  | l/s
454 | 1359 | MIRU Control 4 Air flow set point | Present air flow regulator set point. |  |  | l/s
455 | 1362 | MIRU Control 4 Pressure | Present duct pressure. | 0 | 750 | Pa
456 | 1365 | MIRU Control 4 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
457 | 1368 | MIRU Control 4 External temperature | Present external temperature. | -55.00 | 95.00 | °C
458 | 1371 | MIRU Control 4 Operation time | Present operation time, present in days (24h). | 0 | 9999
459 | 1374 | MIRU Control 4 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
460 | 1377 | MIRU Control 4 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
461 | 1380 | MIRU Control 4 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
462 | 1383 | MIRU Control 4 kWh | kWh value. | 0 | 9999 | kWh
463 | 1386 | MIRU Control 4 MWh | MWh value. | 0 | 32000 | MWh
464 | 1389
465 | 1392
466 | 1395
467 | 1398
468 | 1401 | MIRU Control 5 Min air flow | Min possible air flow setting |  |  | l/s
469 | 1404 | MIRU Control 5 Max air flow | Max possible air flow setting |  |  | l/s
470 | 1407 | MIRU Control 5 Air flow | Present air flow. |  |  | l/s
471 | 1410 | MIRU Control 5 Air flow set point | Present air flow regulator set point. |  |  | l/s
472 | 1413 | MIRU Control 5 Pressure | Present duct pressure. | 0 | 750 | Pa
473 | 1416 | MIRU Control 5 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
474 | 1419 | MIRU Control 5 External temperature | Present external temperature. | -55.00 | 95.00 | °C
475 | 1422 | MIRU Control 5 Operation time | Present operation time, present in days (24h). | 0 | 9999
476 | 1425 | MIRU Control 5 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
477 | 1428 | MIRU Control 5 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
478 | 1431 | MIRU Control 5 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
479 | 1434 | MIRU Control 5 kWh | kWh value. | 0 | 9999 | kWh
480 | 1437 | MIRU Control 5 MWh | MWh value. | 0 | 32000 | MWh
481 | 1440
482 | 1443
483 | 1446
484 | 1449
485 | 1452 | MIRU Control 6 Min air flow | Min possible air flow setting |  |  | l/s
486 | 1455 | MIRU Control 6 Max air flow | Max possible air flow setting |  |  | l/s
487 | 1458 | MIRU Control 6 Air flow | Present air flow. |  |  | l/s
488 | 1461 | MIRU Control 6 Air flow set point | Present air flow regulator set point. |  |  | l/s
489 | 1464 | MIRU Control 6 Pressure | Present duct pressure. | 0 | 750 | Pa
490 | 1467 | MIRU Control 6 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
491 | 1470 | MIRU Control 6 External temperature | Present external temperature. | -55.00 | 95.00 | °C
492 | 1473 | MIRU Control 6 Operation time | Present operation time, present in days (24h). | 0 | 9999
493 | 1476 | MIRU Control 6 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
494 | 1479 | MIRU Control 6 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
495 | 1482 | MIRU Control 6 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
496 | 1485 | MIRU Control 6 kWh | kWh value. | 0 | 9999 | kWh
497 | 1488 | MIRU Control 6 MWh | MWh value. | 0 | 32000 | MWh
498 | 1491
499 | 1494
500 | 1497
501 | 1500
502 | 1503 | MIRU Control 7 Min air flow | Min possible air flow setting |  |  | l/s
503 | 1506 | MIRU Control 7 Max air flow | Max possible air flow setting |  |  | l/s
504 | 1509 | MIRU Control 7 Air flow | Present air flow. |  |  | l/s
505 | 1512 | MIRU Control 7 Air flow set point | Present air flow regulator set point. |  |  | l/s
506 | 1515 | MIRU Control 7 Pressure | Present duct pressure. | 0 | 750 | Pa
507 | 1518 | MIRU Control 7 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
508 | 1521 | MIRU Control 7 External temperature | Present external temperature. | -55.00 | 95.00 | °C
509 | 1524 | MIRU Control 7 Operation time | Present operation time, present in days (24h). | 0 | 9999
510 | 1527 | MIRU Control 7 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
511 | 1530 | MIRU Control 7 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
512 | 1533 | MIRU Control 7 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
513 | 1536 | MIRU Control 7 kWh | kWh value. | 0 | 9999 | kWh
514 | 1539 | MIRU Control 7 MWh | MWh value. | 0 | 32000 | MWh
515 | 1542
516 | 1545
517 | 1548
518 | 1551
519 | 1554 | MIRU Control 8 Min air flow | Min possible air flow setting |  |  | l/s
520 | 1557 | MIRU Control 8 Max air flow | Max possible air flow setting |  |  | l/s
521 | 1560 | MIRU Control 8 Air flow | Present air flow. |  |  | l/s
522 | 1563 | MIRU Control 8 Air flow set point | Present air flow regulator set point. |  |  | l/s
523 | 1566 | MIRU Control 8 Pressure | Present duct pressure. | 0 | 750 | Pa
524 | 1569 | MIRU Control 8 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
525 | 1572 | MIRU Control 8 External temperature | Present external temperature. | -55.00 | 95.00 | °C
526 | 1575 | MIRU Control 8 Operation time | Present operation time, present in days (24h). | 0 | 9999
527 | 1578 | MIRU Control 8 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
528 | 1581 | MIRU Control 8 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
529 | 1584 | MIRU Control 8 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
530 | 1587 | MIRU Control 8 kWh | kWh value. | 0 | 9999 | kWh
531 | 1590 | MIRU Control 8 MWh | MWh value. | 0 | 32000 | MWh
532 | 1593
533 | 1596
534 | 1599
535 | 1602
536 | 1605 | MIRU Control 9 Min air flow | Min possible air flow setting |  |  | l/s
537 | 1608 | MIRU Control 9 Max air flow | Max possible air flow setting |  |  | l/s
538 | 1611 | MIRU Control 9 Air flow | Present air flow. |  |  | l/s
539 | 1614 | MIRU Control 9 Air flow set point | Present air flow regulator set point. |  |  | l/s
540 | 1617 | MIRU Control 9 Pressure | Present duct pressure. | 0 | 750 | Pa
541 | 1620 | MIRU Control 9 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
542 | 1623 | MIRU Control 9 External temperature | Present external temperature. | -55.00 | 95.00 | °C
543 | 1626 | MIRU Control 9 Operation time | Present operation time, present in days (24h). | 0 | 9999
544 | 1629 | MIRU Control 9 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
545 | 1632 | MIRU Control 9 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
546 | 1635 | MIRU Control 9 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
547 | 1638 | MIRU Control 9 kWh | kWh value. | 0 | 9999 | kWh
548 | 1641 | MIRU Control 9 MWh | MWh value. | 0 | 32000 | MWh
549 | 1644
550 | 1647
551 | 1650
552 | 1653
553 | 1656 | MIRU Control 10 Min air flow | Min possible air flow setting |  |  | l/s
554 | 1659 | MIRU Control 10 Max air flow | Max possible air flow setting |  |  | l/s
555 | 1662 | MIRU Control 10 Air flow | Present air flow. |  |  | l/s
556 | 1665 | MIRU Control 10 Air flow set point | Present air flow regulator set point. |  |  | l/s
557 | 1668 | MIRU Control 10 Pressure | Present duct pressure. | 0 | 750 | Pa
558 | 1671 | MIRU Control 10 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
559 | 1674 | MIRU Control 10 External temperature | Present external temperature. | -55.00 | 95.00 | °C
560 | 1677 | MIRU Control 10 Operation time | Present operation time, present in days (24h). | 0 | 9999
561 | 1680 | MIRU Control 10 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
562 | 1683 | MIRU Control 10 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
563 | 1686 | MIRU Control 10 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
564 | 1689 | MIRU Control 10 kWh | kWh value. | 0 | 9999 | kWh
565 | 1692 | MIRU Control 10 MWh | MWh value. | 0 | 32000 | MWh
566 | 1695
567 | 1698
568 | 1701
569 | 1704
Software
570 | 1707 | IQlogic software version | Present controller software version | 0.00 | 99.00
Alarms
604 | 1809 | Triggered alarm #1 | ((Alarm group - 1) x 15) + alarm number in group=Triggered alarm number. Zero if no triggered alarm. | 0 | 1500
605 | 1812 | Triggered alarm #2 |  | 0 | 1500
606 | 1815 | Triggered alarm #3 |  | 0 | 1500
607 | 1818 | Triggered alarm #4 |  | 0 | 1500
608 | 1821 | Triggered alarm #5 |  | 0 | 1500
609 | 1824 | Triggered alarm #6 |  | 0 | 1500
610 | 1827 | Triggered alarm #7 |  | 0 | 1500
611 | 1830 | Triggered alarm #8 |  | 0 | 1500
612 | 1833 | Triggered alarm #9 |  | 0 | 1500
613 | 1836 | Triggered alarm #10 |  | 0 | 1500
614 | 1839 | Triggered alarm group #1 | Zero if no triggered alarm group. | 0 | 100
615 | 1842 | Triggered alarm group #2 |  | 0 | 100
616 | 1845 | Triggered alarm group #3 |  | 0 | 100
617 | 1848 | Triggered alarm group #4 |  | 0 | 100
618 | 1851 | Triggered alarm group #5 |  | 0 | 100
619 | 1854 | Triggered alarm group #6 |  | 0 | 100
620 | 1857 | Triggered alarm group #7 |  | 0 | 100
621 | 1860 | Triggered alarm group #8 |  | 0 | 100
622 | 1863 | Triggered alarm group #9 |  | 0 | 100
623 | 1866 | Triggered alarm group #10 |  | 0 | 100
Time schedule
661 | 1980 | Prolonged low speed remaining hours | Prolonged external low speed remaining operation. | 0 | 23 |  |  | 1.13
662 | 1983 | Prolonged low speed remaining seconds | Prolonged external low speed remaining operation. | 0 | 3600 |  |  | 1.13
663 | 1986 | Prolonged high speed remaining hours | Prolonged external high speed remaining operation. | 0 | 23 |  |  | 1.13
664 | 1989 | Prolonged high speed remaining seconds | Prolonged external high speed remaining operation. | 0 | 3600 |  |  | 1.13
Reserved
680 | 2037
681 | 2040
682 | 2043
683 | 2046
684 | 2049
685 | 2052
686 | 2055
687 | 2058
688 | 2061
689 | 2064
690 | 2067
691 | 2070
692 | 2073
693 | 2076
694 | 2079
695 | 2082
696 | 2085
697 | 2088 | Exhaust heat heat retention at stop |  | 0.00 | 40.00 | °C |  | 2.43
698 | 2091 | Exhaust heat heat retention at operation |  | 0.00 | 40.00 | °C |  | 2.43
699 | 2094 | Exhaust heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 2.43
700 | 2097 | Extra regulation sequence 2 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | % |  | 1.13
701 | 2100 | Extra regulation sequence 2 heat output level | Present level of extra regulation heat. | 0.00 | 100.00 | % |  | 1.13
702 | 2103 | Extra regulation sequence 2 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | % |  | 1.13
703 | 2106 | Extra regulation sequence 2 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | % |  | 1.13
704 | 2109 | Re-heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
705 | 2112 | Re-heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
706 | 2115 | Re-heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
707 | 2118 | Pre-heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
708 | 2121 | Pre-heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
709 | 2124 | Pre-heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
710 | 2127 | Xzone heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
711 | 2130 | Xzone heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
712 | 2133 | Xzone frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
713 | 2136 | Extra regulation sequence 1 heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
714 | 2139 | Extra regulation sequence 1 heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
715 | 2142 | Extra regulation sequence 1 frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
716 | 2145 | Extra regulation sequence 2 heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
717 | 2148 | Extra regulation sequence 2 heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
718 | 2151 | Extra regulation sequence 2 frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
Energy monitoring
719 | 2154 | Heat exchange motor power consumption W |  | 0 | 10000 | W |  | 1.28
720 | 2157 | Heat exchange motor power consumption kW |  | 0.000 | 10.000 | kW |  | 1.28
721 | 2160 | Heat exchange motor energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
722 | 2163 | Heat exchange motor energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
723 | 2166 | Heat power recovery W |  | -999 | 999 | W |  | 1.28
724 | 2169 | Heat power recovery kW |  | -30000 | 30000 | kW |  | 1.28
725 | 2172 | Heat power consumption W |  | -999 | 999 | W |  | 1.28
726 | 2175 | Heat power consumption kW |  | -30000 | 30000 | kW |  | 1.28
727 | 2178 | Cool power recovery W |  | -999 | 999 | W |  | 1.28
728 | 2181 | Cool power recovery kW |  | -30000 | 30000 | kW |  | 1.28
729 | 2184 | Cool power consumption W |  | -999 | 999 | W |  | 1.28
730 | 2187 | Cool power consumption kW |  | -30000 | 30000 | kW |  | 1.28
731 | 2190 | Heat energy recovery kWh |  | 0 | 999 | kWh |  | 1.28
732 | 2193 | Heat energy recovery MWh |  | 0 | 30000 | MWh |  | 1.28
733 | 2196 | Cool energy recovery kWh |  | 0 | 999 | kWh |  | 1.28
734 | 2199 | Cool energy recovery MWh |  | 0 | 30000 | MWh |  | 1.28
735 | 2202 | Heat energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
736 | 2205 | Heat energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
737 | 2208 | Cool energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
738 | 2211 | Cool energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
739 | 2214 | Pulse counter input 1 kWh |  | 0 | 999 | kWh |  | 2.36
740 | 2217 | Pulse counter input 1 MWh |  | 0 | 30000 | MWh |  | 2.36
741 | 2220 | Pulse counter input 2 kWh |  | 0 | 999 | kWh |  | 2.36
742 | 2223 | Pulse counter input 2 MWh |  | 0 | 30000 | MWh |  | 2.36
743 | 2226 | Pulse counter input 3 kWh |  | 0 | 999 | kWh |  | 2.36
744 | 2229 | Pulse counter input 3 MWh |  | 0 | 30000 | MWh |  | 2.36
745 | 2232 | Pulse counter input 4 kWh |  | 0 | 999 | kWh |  | 2.36
746 | 2235 | Pulse counter input 4 MWh |  | 0 | 30000 | MWh |  | 2.36
747 | 2238 | Re-heat water coil power consumption W |  | 0 | 999 | W |  | 2.47
748 | 2241 | Re-heat water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
749 | 2244 | Re-heat water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
750 | 2247 | Re-heat water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
751 | 2250 | Cool water coil power consumption W |  | 0 | 999 | W |  | 2.47
752 | 2253 | Cool water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
753 | 2256 | Cool water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
754 | 2259 | Cool water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
755 | 2262 | Xzone heat water coil power consumption W |  | 0 | 999 | W |  | 2.47
756 | 2265 | Xzone heat water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
757 | 2268 | Xzone heat water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
758 | 2271 | Xzone heat water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
759 | 2274 | Xzone cool water coil power consumption W |  | 0 | 999 | W |  | 2.47
760 | 2277 | Xzone cool water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
761 | 2280 | Xzone cool water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
762 | 2283 | Xzone cool water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
763 | 2286 | Re-heat brine flow level |  | 0.000 | 10.000 | l/s |  | 2.47
764 | 2289 | Cool brine flow level |  | 0.000 | 10.000 | l/s |  | 2.47
765 | 2292 | Xzone heat brine flow level |  | 0.000 | 10.000 | l/s |  | 2.47
766 | 2295 | Xzone cool brine flow level |  | 0.000 | 10.000 | l/s |  | 2.47
767 | 2298
768 | 2301
769 | 2304
770 | 2307
771 | 2310
772 | 2313
773 | 2316
774 | 2319
775 | 2322
776 | 2325
777 | 2328
778 | 2331
779 | 2334
780 | 2337 | Re-heat return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
781 | 2340 | Re-heat feed water temperature |  | 0.00 | 100.00 | °C |  | 2.47
782 | 2343 | Cool return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
783 | 2346 | Cool feed water temperature |  | 0.00 | 100.00 | °C |  | 2.47
784 | 2349 | Xzone heat return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
785 | 2352 | Xzone heat feed water temperature |  | 0.00 | 100.00 | °C |  | 2.47
786 | 2355 | Xzone cool return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
787 | 2358 | Xzone cool feed water temperature |  | 0.00 | 100.00 | °C |  | 2.47
BMS I/O-modules
800 | 2397 | External operation I/O-module 3, analogue input 1 |  | 0.00 | 100.00 | % |  | 1.20
801 | 2400 | External operation I/O-module 3, analogue input 2 |  | 0.00 | 100.00 | % |  | 1.20
802 | 2403
803 | 2406
804 | 2409 | External operation I/O-module 3, analogue output 1 |  | 0.00 | 100.00 | % |  | 1.20
805 | 2412 | External operation I/O-module 3, analogue output 2 |  | 0.00 | 100.00 | % |  | 1.20
806 | 2415 | External operation I/O-module 6, analogue input 1 |  | 0.00 | 100.00 | % |  | 1.20
807 | 2418 | External operation I/O-module 6, analogue input 2 |  | 0.00 | 100.00 | % |  | 1.20
808 | 2421
809 | 2424
810 | 2427 | External operation I/O-module 6, analogue output 1 |  | 0.00 | 100.00 | % |  | 1.20
811 | 2430 | External operation I/O-module 6, analogue output 2 |  | 0.00 | 100.00 | % |  | 1.20
812 | 2433 | External operation I/O-module A, analogue input |  | 0.00 | 100.00 | % |  | 1.20
813 | 2436 | External operation I/O-module A, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
814 | 2439 | External operation I/O-module A, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
815 | 2442 | External operation I/O-module B, analogue input |  | 0.00 | 100.00 | % |  | 1.20
816 | 2445 | External operation I/O-module B, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
817 | 2448 | External operation I/O-module B, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
818 | 2451 | External operation I/O-module C, analogue input |  | 0.00 | 100.00 | % |  | 1.20
819 | 2454 | External operation I/O-module C, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
820 | 2457 | External operation I/O-module C, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
Alarms
1001 | 3000 | Alarm group 1 | Bit0=Alarm1 Bit1=Alarm2 Bit2=Alarm3 Bit3=Alarm4 Bit4=Alarm5 Bit5=Alarm6 Bit6=Alarm7 Bit7=Alarm8 Bit8=Alarm9 Bit9=Alarm10 Bit10=Alarm11 Bit11=Alarm12 Bit12=Alarm13 Bit13=Alarm14 Bit14=Alarm15 | 0 | 32767
1002 | 3003 | Alarm group 2 |  | 0 | 32767
1003 | 3006 | Alarm group 3 |  | 0 | 32767
1004 | 3009 | Alarm group 4 |  | 0 | 32767
1005 | 3012 | Alarm group 5 |  | 0 | 32767
1006 | 3015 | Alarm group 6 |  | 0 | 32767
1007 | 3018 | Alarm group 7 |  | 0 | 32767
1008 | 3021 | Alarm group 8 |  | 0 | 32767
1009 | 3024 | Alarm group 9 |  | 0 | 32767
1010 | 3027 | Alarm group 10 |  | 0 | 32767
1011 | 3030 | Alarm group 11 |  | 0 | 32767
1012 | 3033 | Alarm group 12 |  | 0 | 32767
1013 | 3036 | Alarm group 13 |  | 0 | 32767
1014 | 3039 | Alarm group 14 |  | 0 | 32767
1015 | 3042 | Alarm group 15 |  | 0 | 32767
1016 | 3045 | Alarm group 16 |  | 0 | 32767
1017 | 3048 | Alarm group 17 |  | 0 | 32767
1018 | 3051 | Alarm group 18 |  | 0 | 32767
1019 | 3054 | Alarm group 19 |  | 0 | 32767
1020 | 3057 | Alarm group 20 |  | 0 | 32767
1021 | 3060 | Alarm group 21 |  | 0 | 32767
1022 | 3063 | Alarm group 22 |  | 0 | 32767
1023 | 3066 | Alarm group 23 |  | 0 | 32767
1024 | 3069 | Alarm group 24 |  | 0 | 32767
1025 | 3072 | Alarm group 25 |  | 0 | 32767
1026 | 3075 | Alarm group 26 |  | 0 | 32767
1027 | 3078 | Alarm group 27 |  | 0 | 32767
1028 | 3081 | Alarm group 28 |  | 0 | 32767
1029 | 3084 | Alarm group 29 |  | 0 | 32767
1030 | 3087 | Alarm group 30 |  | 0 | 32767
1031 | 3090 | Alarm group 31 |  | 0 | 32767
1032 | 3093 | Alarm group 32 |  | 0 | 32767
1033 | 3096 | Alarm group 33 |  | 0 | 32767
1034 | 3099 | Alarm group 34 |  | 0 | 32767
1035 | 3102 | Alarm group 35 |  | 0 | 32767
1036 | 3105 | Alarm group 36 |  | 0 | 32767
1037 | 3108 | Alarm group 37 |  | 0 | 32767
1038 | 3111 | Alarm group 38 |  | 0 | 32767
1039 | 3114 | Alarm group 39 |  | 0 | 32767
1040 | 3117 | Alarm group 40 |  | 0 | 32767
1041 | 3120 | Alarm group 41 |  | 0 | 32767
1042 | 3123 | Alarm group 42 |  | 0 | 32767
1043 | 3126 | Alarm group 43 |  | 0 | 32767
1044 | 3129 | Alarm group 44 |  | 0 | 32767
1045 | 3132 | Alarm group 45 |  | 0 | 32767
1046 | 3135 | Alarm group 46 |  | 0 | 32767
1047 | 3138 | Alarm group 47 |  | 0 | 32767
1048 | 3141 | Alarm group 48 |  | 0 | 32767
1049 | 3144 | Alarm group 49 |  | 0 | 32767
1050 | 3147 | Alarm group 50 |  | 0 | 32767
1051 | 3150 | Alarm group 51 |  | 0 | 32767
1052 | 3153 | Alarm group 52 |  | 0 | 32767
1053 | 3156 | Alarm group 53 |  | 0 | 32767
1054 | 3159 | Alarm group 54 |  | 0 | 32767
1055 | 3162 | Alarm group 55 |  | 0 | 32767
1056 | 3165 | Alarm group 56 |  | 0 | 32767
1057 | 3168 | Alarm group 57 |  | 0 | 32767
1058 | 3171 | Alarm group 58 |  | 0 | 32767
1059 | 3174 | Alarm group 59 |  | 0 | 32767
1060 | 3177 | Alarm group 60 |  | 0 | 32767
1061 | 3180 | Alarm group 61 |  | 0 | 32767
1062 | 3183 | Alarm group 62 |  | 0 | 32767
1063 | 3186 | Alarm group 63 |  | 0 | 32767
1064 | 3189 | Alarm group 64 |  | 0 | 32767
1065 | 3192 | Alarm group 65 |  | 0 | 32767
1066 | 3195 | Alarm group 66 |  | 0 | 32767
1067 | 3198 | Alarm group 67 |  | 0 | 32767
1068 | 3201 | Alarm group 68 |  | 0 | 32767
1069 | 3204 | Alarm group 69 |  | 0 | 32767
1070 | 3207 | Alarm group 70 |  | 0 | 32767
1071 | 3210 | Alarm group 71 |  | 0 | 32767
1072 | 3213 | Alarm group 72 |  | 0 | 32767
1073 | 3216 | Alarm group 73 |  | 0 | 32767
1074 | 3219 | Alarm group 74 |  | 0 | 32767
1075 | 3222 | Alarm group 75 |  | 0 | 32767
1076 | 3225 | Alarm group 76 |  | 0 | 32767
1077 | 3228 | Alarm group 77 |  | 0 | 32767
1078 | 3231 | Alarm group 78 |  | 0 | 32767
1079 | 3234 | Alarm group 79 |  | 0 | 32767
1080 | 3237 | Alarm group 80 |  | 0 | 32767
1081 | 3240 | Alarm group 81 |  | 0 | 32767
1082 | 3243 | Alarm group 82 |  | 0 | 32767
1083 | 3246 | Alarm group 83 |  | 0 | 32767
1084 | 3249 | Alarm group 84 |  | 0 | 32767
1085 | 3252 | Alarm group 85 |  | 0 | 32767
1086 | 3255 | Alarm group 86 |  | 0 | 32767
1087 | 3258 | Alarm group 87 |  | 0 | 32767
1088 | 3261 | Alarm group 88 |  | 0 | 32767
1089 | 3264 | Alarm group 89 |  | 0 | 32767
1090 | 3267 | Alarm group 90 |  | 0 | 32767
1091 | 3270 | Alarm group 91 |  | 0 | 32767
1092 | 3273 | Alarm group 92 |  | 0 | 32767
1093 | 3276 | Alarm group 93 |  | 0 | 32767
1094 | 3279 | Alarm group 94 |  | 0 | 32767
1095 | 3282 | Alarm group 95 |  | 0 | 32767
1096 | 3285 | Alarm group 96 |  | 0 | 32767
1097 | 3288 | Alarm group 97 |  | 0 | 32767
1098 | 3291 | Alarm group 98 |  | 0 | 32767
1099 | 3294 | Alarm group 99 |  | 0 | 32767
1100 | 3297 | Alarm group 100 |  | 0 | 32767
H/C
1405 | 4212 | H/C recirculation defrost damper output |  | 0.00 | 100.00 | % |  | 1.23
1406 | 4215 | H/C recirculation defrost damper input |  | 0.00 | 100.00 | % |  | 1.23
1407 | 4218
1408 | 4221
1409 | 4224 | H/C heat anti frost temp/overheat input | Present H/C heat anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 1.23
1410 | 4227
1411 | 4230
1412 | 4233
1413 | 4236 | H/C operation level |  | 0.00 | 100.00 | % |  | 1.23
1414 | 4239 | H/C heat defrost level |  | 0.00 | 100.00 | % |  | 1.23
1415 | 4242 | H/C defrost pressure level |  | -500.0 | 2500.0 | Pa |  | 1.23
1416 | 4245 | H/C defrost pressure start limit |  | 0.0 | 1000.0 | Pa |  | 1.23
1417 | 4248 | H/C defrost pressure end limit |  | 0.0 | 1000.0 | Pa |  | 1.23
1418 | 4251 | H/C superheat temp |  | 0.0 | 99.0 | K |  | 1.23
1419 | 4254 | H/C discharge temp |  | -10.0 | 130.0 | °C |  | 1.23
1420 | 4257 | H/C suction temp |  | -40.0 | 105.0 | °C |  | 1.23
1421 | 4260 | H/C condensation temp |  | 0.0 | 1000.0 | °C |  | 1.23
1422 | 4263 | H/C evaporation temp |  | 0.0 | 1000.0 | °C |  | 1.23
1423 | 4266 | H/C high pressure |  | 0.10 | 50.00 | Bar |  | 1.23
1424 | 4269 | H/C low pressure |  | 0.10 | 50.00 | Bar |  | 1.23

## Vpac 3 (RO)
GOLD_E_F_EXOline_250905
Index var. Vpac 3 (RO)
Index | Cell nbr | Name | Description | Min | Max | Unit | Default | Misc
AHU Air flow/duct pressure
1 | 0
2 | 1 | Application id/AHU Type | 10=GOLD RX, 11=GOLD PX, 12=GOLD CX, 13=GOLD SD/SA,14=GOLD SD/EA, 15=GOLD SD/SA+CX, 16=GOLD SD/SA+EA, 17=GOLD SD/SA+EA+CX | 0 | 999
3 | 2 | Air flow direction | 0=Fan no.2 as SA, 1=Fan no.1 as SA. | 0 | 1
4 | 3
5 | 4
AHU heat exchange
110 | 109 | PHX bypass type | 0=Center, 1=Side | 0 | 1 |  |  | 2.43
111 | 110
112 | 111 | PX exchanger bypass 4A output |  | 0.00 | 100.00 | % |  | 2.43
113 | 112 | PX exchanger bypass 4A feedback |  | 0.00 | 100.00 | % |  | 2.43
114 | 113 | PHX-2 3D Type | 0=Cross flow, 1=Counter flow | 0 | 1 |  |  | 1.21
115 | 114 | PHX type | 0=PHX-1, one damper and humidity sensor, 1=PHX-2, three dampers, 2=PHX-3, one damper and pressure sensor. | 0 | 2 |  |  | 1.16
AHU Coils
140 | 139 | Extra regulation sequence 1 coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
141 | 140
142 | 141 | Extra regulation sequence 2 coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15 |  |  | 1.13
143 | 142
144 | 143
145 | 144
146 | 145
147 | 146
148 | 147
149 | 148
150 | 149
151 | 150
152 | 151 | Re-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
153 | 152
154 | 153
155 | 154
156 | 155
157 | 156
158 | 157
159 | 158
160 | 159
161 | 160
162 | 161
163 | 162 | Cool coil type | 0=None,1..8=N/A, 9..10=Water, 11..15=N/A | 0 | 15
164 | 163
Xzone coils
198 | 197 | Xzone heat, coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
199 | 198
Pre-heat
220 | 219
221 | 220
222 | 221
223 | 222
224 | 223 | Pre-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
225 | 224
Exhaust heat
284 | 283 | Exhaust heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15 |  |  | 2.43
SMART Link
320 | 319 | SMART Link, DX cool mode
321 | 320
AHU Version
591 | 590 | AHU Version | 1=Version 1 2=Version 2 3=Version 3 4=Version 4 5=Version A 6=Version B 7=Version C 8=Version D 9=Version E 10=Version F |  |  |  |  | 2.44
Operation level
592 | 591 | Operation level | 0=Fan not available 1=Alarm stop 2=Manual total stop (on hand terminal) 3=External total stop (digital input) 4=Communication total stop 5=Communication normal stop 6=Communication extended normal stop 7=Time channel total stop 8=Time channel normal stop 9=Time channel extended normal stop 10=Low speed=normal stop 11=SA Fan starting up 12=Fan regulation blocked 13=ReCO2 100% recirculation(1.11) 14=Morning boost stop(1.11) 15=Intermittent night heat stop(1.11) 16=After cooling electric heater 17=COOL DX switch off delay 18=Damper switch off delay 19=Manual low speed (on hand terminal) 20=External low speed (digital input) 21=Extended external low speed 22=Communication low speed 23=Time channel low speed 24=Morning boost low speed 25=Intermittent night heat low speed 26=Manual high speed (on hand terminal) 27=External high speed (digital input) 28=Extended external high speed 29=Communication high speed 30=Time channel high speed 31=Summer night cooling high speed 32=Filter calibration 33=RHX Defrost calibration 34=ReCO2 calibration 35=AHU start up 36=Re-heat ramp down 37=HX ramp down 38=Air adjustment 39=Fans in operation with active fire alarm 40=PX bypass damper adjustment(1.12) | 0 | 100 |  |  | 1.12
593 | 592
Time schedule
654 | 653 | Weekday | The internal clock present weekday | 1 | 7
655 | 654 | Current action | 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5
656 | 655 | Effective period | 0=Inactive, 1=Active | 0 | 1
657 | 656 | Exception schedule 1 | 0=Inactive, 1=Active | 0 | 1
658 | 657 | Exception schedule 2 | 0=Inactive, 1=Active | 0 | 1
659 | 658 | Calendar 1 | 0=Inactive, 1=Active | 0 | 1
660 | 659 | Calendar 2 | 0=Inactive, 1=Active | 0 | 1
665 | 664 | Schedule exception invalid data | 0=Inactive, 1=Active | 0 | 1 |  |  | 2.34
666 | 665 | Calendar 1 invalid data | 0=Inactive, 1=Active | 0 | 1 |  |  | 2.34
667 | 666 | Calendar 2 invalid data | 0=Inactive, 1=Active | 0 | 1 |  |  | 2.34
H/C
1400 | 1399 | H/C mode | 0=Inactive, 1=Active | 0 | 1 |  |  | 1.23
1401 | 1400 | H/C defrost accessory | 0=Inactive, 1=Recirculation, 2=Electric heat | 0 | 2 |  |  | 1.23
1402 | 1401 | H/C recirculation defrost active | 0=Inactive, 1=Active | 0 | 1 |  |  | 1.31
1403 | 1402 | H/C defrost active | 0=Inactive, 1=Active | 0 | 1 |  |  | 1.31
1404 | 1403
1405 | 1404
1406 | 1405
1407 | 1406 | H/C heat type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15 |  |  | 1.23
1408 | 1407
1409 | 1408
1410 | 1409 | H/C operation mode | 0=Inactive, 1=Stop, 2=Stabilization, 3=Normal operation, 4=Comfort operation, 5=Economy operation, 6=Defrost, 7=Defrost, 8=Oil recovery | 0 | 8 |  |  | 1.23
1411 | 1410 | H/C defrost mode | 0=Inactive, 1=Start delay, 2=Initializing, 3=Pre-defrosting, 4=Defrosting, 5=Draining | 0 | 5 |  |  | 1.23
1412 | 1411 | H/C heat/cool mode | 0=Heating, 1=Cooling | 0 | 1 |  |  | 1.23

## Vpac 4 (RO)
GOLD_E_F_EXOline_250905
Logical var. Vpac 4 (RO) 1bit
Index | Cell nbr | Name | Description | Min | Max | Unit | Default | Misc
Operation level/alarm
1 | 0 | Operation active | Relay output status | 0 | 1
2 | 1 | Damper operation active | Relay output status | 0 | 1
3 | 2 | Low speed operation active | Low speed operation status | 0 | 1
4 | 3 | High speed operation active | High speed operation status | 0 | 1
5 | 4 | Intermittent night heat active |  | 0 | 1
6 | 5 | Morning boost active |  | 0 | 1
7 | 6 | Heating boost active |  | 0 | 1
8 | 7 | Cooling boost active |  | 0 | 1
9 | 8 | Summer night cool active |  | 0 | 1
10 | 9
11 | 10
12 | 11
13 | 12 | A-alarm active | Any alarm with priority class A active | 0 | 1
14 | 13 | B-alarm active | Any alarm with priority class B active | 0 | 1
15 | 14
16 | 15
Heat exchange
17 | 16 | HX operation active | HX status | 0 | 1
18 | 17 | HX cool recovery active | HX cool recovery status | 0 | 1
19 | 18 | HX defrost active | HX defrost status | 0 | 1
20 | 19
21 | 20
22 | 21 | RHX speed monitor signal | RHX speed monitor status | 0 | 1
23 | 22
24 | 23
25 | 24
26 | 25
27 | 26 | CHX-1 pump output | CHX-1 relay output status | 0 | 1
28 | 27 | CHX-1 pump input | CHX-1 digital input status | 0 | 1
29 | 28
30 | 29 | Seasonal controlled temperature regulation indication |  | 0 | 1 |  |  | 2.46
AHU Coils
31 | 30 | Season heat, extra regulation sequence allowed |  | 0 | 1
32 | 31 | Season heat, re-heat allowed |  | 0 | 1
33 | 32 | Extra regulation sequence 1, output | Relay output status | 0 | 1
34 | 33 | Extra regulation sequence 1, power reduction active |  | 0 | 1
35 | 34 | Extra regulation sequence 1, anti-frost regulation active |  | 0 | 1
36 | 35 | Extra regulation sequence 1 combi coil input |  | 0 | 1 |  |  | 2.37
37 | 36 | Extra regulation sequence 1 combi coil output |  | 0 | 1 |  |  | 2.37
38 | 37 | Re-heat output | Relay output status | 0 | 1
39 | 38 | Re-heat power reduction active |  | 0 | 1
40 | 39 | Re-heat anti-frost regulation active |  | 0 | 1
41 | 40
42 | 41
43 | 42 | Cool output 1 | Relay output status | 0 | 1
44 | 43 | Cool output 2 | Relay output status | 0 | 1
45 | 44
46 | 45 | Extra regulation sequence 2 combi coil input |  | 0 | 1 |  |  | 2.37
47 | 46 | Extra regulation sequence 2 combi coil output |  | 0 | 1 |  |  | 2.37
48 | 47 | Extra regulation sequence 2, output | Relay output status | 0 | 1 |  |  | 1.13
49 | 48 | Extra regulation sequence 2, power reduction active |  | 0 | 1 |  |  | 1.13
50 | 49 | Extra regulation sequence 2, anti-frost regulation active |  | 0 | 1 |  |  | 1.13
Pre-heat
51 | 50 | Pre-heat output | Relay output status | 0 | 1
52 | 51 | Pre-heat power reduction active |  | 0 | 1
53 | 52 | Pre-heat anti-frost regulation active |  | 0 | 1
54 | 53
55 | 54
Xzone
56 | 55 | Xzone heat output | Relay output status | 0 | 1
57 | 56 | Xzone heat power reduction active
58 | 57 | Xzone heat anti-frost regulation active
59 | 58
60 | 59
61 | 60
62 | 61
63 | 62 | Xzone cool output 1 | Relay output status | 0 | 1
64 | 63 | Xzone cool output 2 | Relay output status | 0 | 1
65 | 64 | Xzone combi coil module A input | Xzone combi coil module A digital input status | 0 | 1 |  |  | 2.43
66 | 65 | Xzone combi coil module A output | Relay output status | 0 | 1 |  |  | 2.43
67 | 66 | Xzone combi coil module B input | Xzone combi coil module B digital input status | 0 | 1 |  |  | 2.43
68 | 67 | Xzone combi coil module B output | Relay output status | 0 | 1 |  |  | 2.43
69 | 68
70 | 69
Exhaust heat
71 | 70
72 | 71
73 | 72
74 | 73
75 | 74 | Exhaust heat pump output | Relay output status | 0 | 1 |  |  | 2.43
76 | 75 | Exhaust heat heating power reduction active |  | 0 | 1 |  |  | 2.43
77 | 76 | Exhaust heat anti-frost regulation active |  | 0 | 1 |  |  | 2.43
78 | 77
79 | 78
80 | 79
81 | 80
82 | 81
83 | 82
84 | 83
85 | 84
86 | 85
87 | 86
88 | 87
89 | 88
90 | 89
91 | 90
92 | 91
93 | 92
94 | 93
95 | 94
96 | 95
97 | 96
98 | 97
AYC
99 | 98 | AYC heat pump output | Relay output status | 0 | 1
100 | 99 | AYC heat pump input | Digital input status | 0 | 1
101 | 100
102 | 101
103 | 102
104 | 103 | AYC cool pump output | Relay output status | 0 | 1
105 | 104 | AYC cool pump input | Digital input status | 0 | 1
106 | 105
107 | 106
108 | 107
COOL DX
109 | 108 | COOL DX compressor 1 output | Relay output status | 0 | 1
110 | 109 | COOL DX compressor 1 input | Digital input status | 0 | 1
111 | 110
112 | 111
113 | 112
114 | 113
115 | 114 | COOL DX compressor 2 output | Relay output status | 0 | 1
116 | 115 | COOL DX compressor 2 input | Digital input status | 0 | 1
117 | 116
Wireless AP active
199 | 198 | Wireless AP active |  | 0 | 1 |  | 0 | 2.43
BMS I/O-modules
200 | 199 | External operation I/O-module 3, digital input 1 |  | 0 | 1 |  |  | 1.20
201 | 200 | External operation I/O-module 3, digital input 2 |  | 0 | 1 |  |  | 1.20
202 | 201 | External operation I/O-module 3, digital output 1 |  | 0 | 1 |  |  | 1.20
203 | 202 | External operation I/O-module 3, digital output 2 |  | 0 | 1 |  |  | 1.20
204 | 203 | External operation I/O-module 6, digital input 1 |  | 0 | 1 |  |  | 1.20
205 | 204 | External operation I/O-module 6, digital input 2 |  | 0 | 1 |  |  | 1.20
206 | 205 | External operation I/O-module 6, digital output 1 |  | 0 | 1 |  |  | 1.20
207 | 206 | External operation I/O-module 6, digital output 2 |  | 0 | 1 |  |  | 1.20
208 | 207 | External operation I/O-module A, digital input |  | 0 | 1 |  |  | 1.20
209 | 208 | External operation I/O-module B, digital input |  | 0 | 1 |  |  | 1.20
210 | 209 | External operation I/O-module C, digital input |  | 0 | 1 |  |  | 1.20
SMART Link
319 | 318 | SMART Link, DX operation
320 | 319
321 | 320
322 | 321
323 | 322 | SMART Link, DX unit 1 operation |  | 0 | 1
324 | 323 | SMART Link, DX unit 1 cool mode |  | 0 | 1
325 | 324 | SMART Link, DX unit 1 defrost request |  | 0 | 1
326 | 325 | SMART Link, DX unit 1 defrost active |  | 0 | 1
327 | 326
328 | 327
329 | 328
330 | 329
331 | 330
332 | 331
333 | 332
334 | 333 | SMART Link, DX unit 2 operation |  | 0 | 1
335 | 334 | SMART Link, DX unit 2 cool mode |  | 0 | 1
336 | 335 | SMART Link, DX unit 2 defrost request |  | 0 | 1
337 | 336 | SMART Link, DX unit 2 defrost active |  | 0 | 1
338 | 337
339 | 338
340 | 339
341 | 340
342 | 341
343 | 342
344 | 343
345 | 344 | SMART Link, DX unit 3 operation |  | 0 | 1
346 | 345 | SMART Link, DX unit 3 cool mode |  | 0 | 1
347 | 346 | SMART Link, DX unit 3 defrost request |  | 0 | 1
348 | 347 | SMART Link, DX unit 3 defrost active |  | 0 | 1
349 | 348
350 | 349
351 | 350
352 | 351
353 | 352
354 | 353
355 | 354
356 | 355 | SMART Link, DX unit 4 operation |  | 0 | 1
357 | 356 | SMART Link, DX unit 4 cool mode |  | 0 | 1
358 | 357 | SMART Link, DX unit 4 defrost request |  | 0 | 1
359 | 358 | SMART Link, DX unit 4 defrost active |  | 0 | 1
360 | 359
361 | 360
362 | 361
363 | 362
364 | 363
365 | 364
366 | 365
367 | 366 | SMART Link, DX Defrost airflow increase status |  | 0 | 1 |  |  | 1.26
368 | 367
Alarms
501 | 500 | Active alarm 1 | Alarm 1:1 External fire alarm no. 1 tripped | 0 | 1
502 | 501 | Active alarm 2 | Alarm 1:2 External fire alarm no. 2 tripped | 0 | 1
503 | 502 | Active alarm 3 | Alarm 1:3 Internal fire alarm tripped | 0 | 1
504 | 503 | Active alarm 4 |  | 0 | 1
505 | 504 | Active alarm 5 |  | 0 | 1
506 | 505 | Active alarm 6 |  | 0 | 1
507 | 506 | Active alarm 7 |  | 0 | 1
508 | 507 | Active alarm 8 |  | 0 | 1
509 | 508 | Active alarm 9 |  | 0 | 1
510 | 509 | Active alarm 10 |  | 0 | 1
511 | 510 | Active alarm 11 |  | 0 | 1
512 | 511 | Active alarm 12 |  | 0 | 1
513 | 512 | Active alarm 13 |  | 0 | 1
514 | 513 | Active alarm 14 |  | 0 | 1
515 | 514 | Active alarm 15 |  | 0 | 1
516 | 515 | Active alarm 16 | Alarm 2:1 External alarm no. 1 tripped | 0 | 1
517 | 516 | Active alarm 17 | Alarm 2:2 External alarm no. 2 tripped | 0 | 1
518 | 517 | Active alarm 18 |  | 0 | 1
519 | 518 | Active alarm 19 |  | 0 | 1
520 | 519 | Active alarm 20 |  | 0 | 1
521 | 520 | Active alarm 21 |  | 0 | 1
522 | 521 | Active alarm 22 |  | 0 | 1
523 | 522 | Active alarm 23 |  | 0 | 1
524 | 523 | Active alarm 24 |  | 0 | 1
525 | 524 | Active alarm 25 |  | 0 | 1
526 | 525 | Active alarm 26 |  | 0 | 1
527 | 526 | Active alarm 27 |  | 0 | 1
528 | 527 | Active alarm 28 |  | 0 | 1
529 | 528 | Active alarm 29 |  | 0 | 1
530 | 529 | Active alarm 30 |  | 0 | 1
531 | 530 | Active alarm 31 | Alarm 3:1 Pre-heat, I/O-module no. 9 communication error | 0 | 1
532 | 531 | Active alarm 32 | Alarm 3:2 Pre-heat, electrical heater overheat protection tripped | 0 | 1
533 | 532 | Active alarm 33 | Alarm 3:3 Pre-heat, frost protection tripped | 0 | 1
534 | 533 | Active alarm 34 | Alarm 3:4 Pre-heat, frost protection temperature sensor defective | 0 | 1
535 | 534 | Active alarm 35 | Alarm 3:5 Pre-heat, temperature sensor defective | 0 | 1
536 | 535 | Active alarm 36 | Alarm 3:6 Pre-heat, valve monitoring tripped | 0 | 1
537 | 536 | Active alarm 37 | Alarm 3:7 Pre-heat, temperature below set point alarm limit | 0 | 1
538 | 537 | Active alarm 38 | Alarm 3:8 Pre-heat, alarm input tripped | 0 | 1 |  |  | 1.10
539 | 538 | Active alarm 39 |  | 0 | 1
540 | 539 | Active alarm 40 |  | 0 | 1
541 | 540 | Active alarm 41 |  | 0 | 1
542 | 541 | Active alarm 42 |  | 0 | 1
543 | 542 | Active alarm 43 |  | 0 | 1
544 | 543 | Active alarm 44 |  | 0 | 1
545 | 544 | Active alarm 45 |  | 0 | 1
546 | 545 | Active alarm 46 | Alarm 4:1 Extra regulation sequence 1, I/O-module no. E communication error | 0 | 1 |  |  | 1.13
547 | 546 | Active alarm 47 | Alarm 4:2 Extra regulation sequence 1, electrical heater overheat protection tripped | 0 | 1 |  |  | 1.13
548 | 547 | Active alarm 48 | Alarm 4:3 Extra regulation sequence 1, frost protection tripped | 0 | 1 |  |  | 1.13
549 | 548 | Active alarm 49 | Alarm 4:4 Extra regulation sequence 1, frost protection temperature sensor defective | 0 | 1 |  |  | 1.13
550 | 549 | Active alarm 50 | Alarm 4:5 Extra regulation sequence 1, valve monitoring tripped | 0 | 1 |  |  | 1.13
551 | 550 | Active alarm 51 | Alarm 4:6 Extra regulation sequence 1, alarm input tripped | 0 | 1 |  |  | 1.13
552 | 551 | Active alarm 52 | Alarm 4:7 Extra regulation sequence 1, temperature protection from communication error | 0 | 1 |  |  | 1.13
553 | 552 | Active alarm 53 | Alarm 4:8 Extra regulation sequence 1 combi coil temperature sensor defective | 0 | 1 |  |  | 1.26
554 | 553 | Active alarm 54 | Alarm 4:9 Extra regulation sequence 2, I/O-module no. F communication error | 0 | 1 |  |  | 1.13
555 | 554 | Active alarm 55 | Alarm 4:10 Extra regulation sequence 2, electrical heater overheat protection tripped | 0 | 1 |  |  | 1.13
556 | 555 | Active alarm 56 | Alarm 4:11 Extra regulation sequence 2, frost protection tripped | 0 | 1 |  |  | 1.13
557 | 556 | Active alarm 57 | Alarm 4:12 Extra regulation sequence 2, frost protection temperature sensor defective | 0 | 1 |  |  | 1.13
558 | 557 | Active alarm 58 | Alarm 4:13 Extra regulation sequence 2, valve monitoring tripped | 0 | 1 |  |  | 1.13
559 | 558 | Active alarm 59 | Alarm 4:14 Extra regulation sequence 2, alarm input tripped | 0 | 1 |  |  | 1.13
560 | 559 | Active alarm 60 | Alarm 4:15 Extra regulation sequence 2 combi coil temperature sensor defective | 0 | 1 |  |  | 1.26
561 | 560 | Active alarm 61 | Alarm 5:1 Re-heat, electrical heater over heat protection tripped | 0 | 1
562 | 561 | Active alarm 62 | Alarm 5:2 Re-heat, frost protection tripped | 0 | 1
563 | 562 | Active alarm 63 | Alarm 5:3 Re-heat, frost protection temperature sensor defective | 0 | 1
564 | 563 | Active alarm 64 | Alarm 5:4 Re-heat, heat valve monitoring tripped | 0 | 1
565 | 564 | Active alarm 65 | Alarm 5:5 Re-heat alarm input tripped | 0 | 1 |  |  | 1.27
566 | 565 | Active alarm 66 |  | 0 | 1
567 | 566 | Active alarm 67 |  | 0 | 1
568 | 567 | Active alarm 68 |  | 0 | 1
569 | 568 | Active alarm 69 |  | 0 | 1
570 | 569 | Active alarm 70 |  | 0 | 1
571 | 570 | Active alarm 71 |  | 0 | 1
572 | 571 | Active alarm 72 |  | 0 | 1
573 | 572 | Active alarm 73 |  | 0 | 1
574 | 573 | Active alarm 74 |  | 0 | 1
575 | 574 | Active alarm 75 |  | 0 | 1
576 | 575 | Active alarm 76 | Alarm 6:1 Xzone, I/O-module no. A communication error | 0 | 1
577 | 576 | Active alarm 77 | Alarm 6:2 Xzone, electrical heater overheat protection tripped | 0 | 1
578 | 577 | Active alarm 78 | Alarm 6:3 Xzone, frost protection tripped | 0 | 1
579 | 578 | Active alarm 79 | Alarm 6:4 Xzone, frost protection temperature sensor defective | 0 | 1
580 | 579 | Active alarm 80 | Alarm 6:5 Xzone, supply air temperature sensor defective | 0 | 1
581 | 580 | Active alarm 81 | Alarm 6:6 Xzone, heat valve monitoring tripped | 0 | 1
582 | 581 | Active alarm 82 | Alarm 6:7 Xzone, supply air temperature below set point alarm limit | 0 | 1
583 | 582 | Active alarm 83 | Alarm 6:8 Xzone, supply air temperature above set point alarm limit | 0 | 1
584 | 583 | Active alarm 84 | Alarm 6:9 Xzone, heat alarm input tripped | 0 | 1 |  |  | 1.10
585 | 584 | Active alarm 85 | Alarm 6:10 Xzone combi coil module A temperature sensor defective | 0 | 1 |  |  | 2.43
586 | 585 | Active alarm 86 | Alarm 6:11 Xzone temperature protection, I/O-module no. 9 com. Error | 0 | 1 |  |  | 2.43
587 | 586 | Active alarm 87 |  | 0 | 1
588 | 587 | Active alarm 88 |  | 0 | 1
589 | 588 | Active alarm 89 |  | 0 | 1
590 | 589 | Active alarm 90 |  | 0 | 1
591 | 590 | Active alarm 91 | Alarm 7:1 Xzone, I/O-module no. B communication error | 0 | 1
592 | 591 | Active alarm 92 | Alarm 7:2 Xzone, extract air temperature sensor defective | 0 | 1
593 | 592 | Active alarm 93 | Alarm 7:3 Xzone, cool valve monitoring tripped | 0 | 1
594 | 593 | Active alarm 94 | Alarm 7:4 Xzone, extract air temperature below alarm limit | 0 | 1
595 | 594 | Active alarm 95 | Alarm 7:5 Xzone, cool alarm input 1 tripped | 0 | 1 |  |  | 1.10
596 | 595 | Active alarm 96 | Alarm 7:6 Xzone, cool alarm input 2 tripped | 0 | 1 |  |  | 1.10
597 | 596 | Active alarm 97 | Alarm 7:7 Xzone combi coil module B temperature sensor defective | 0 | 1 |  |  | 2.43
598 | 597 | Active alarm 98 |  | 0 | 1
599 | 598 | Active alarm 99 |  | 0 | 1
600 | 599 | Active alarm 100 |  | 0 | 1
601 | 600 | Active alarm 101 |  | 0 | 1
602 | 601 | Active alarm 102 |  | 0 | 1
603 | 602 | Active alarm 103 |  | 0 | 1
604 | 603 | Active alarm 104 |  | 0 | 1
605 | 604 | Active alarm 105 |  | 0 | 1
606 | 605 | Active alarm 106 |  | 0 | 1
607 | 606 | Active alarm 107 |  | 0 | 1
608 | 607 | Active alarm 108 |  | 0 | 1
609 | 608 | Active alarm 109 |  | 0 | 1
610 | 609 | Active alarm 110 | Alarm 8:5 Cool valve monitoring tripped | 0 | 1
611 | 610 | Active alarm 111 | Alarm 8:6 Cool alarm input 1 tripped | 0 | 1 |  |  | 1.27
612 | 611 | Active alarm 112 | Alarm 8:7 Cool alarm input 2 tripped | 0 | 1 |  |  | 1.27
613 | 612 | Active alarm 113 |  | 0 | 1
614 | 613 | Active alarm 114 |  | 0 | 1
615 | 614 | Active alarm 115 |  | 0 | 1
616 | 615 | Active alarm 116 |  | 0 | 1
617 | 616 | Active alarm 117 |  | 0 | 1
618 | 617 | Active alarm 118 |  | 0 | 1
619 | 618 | Active alarm 119 |  | 0 | 1
620 | 619 | Active alarm 120 |  | 0 | 1
621 | 620 | Active alarm 121 | Alarm 9:1 Exhaust heat I/O-module no. 4 com error | 0 | 1 |  |  | 2.43
622 | 621 | Active alarm 122 | Alarm 9:2 Exhaust heat electrical heater overheat protection tripped | 0 | 1 |  |  | 2.43
623 | 622 | Active alarm 123 | Alarm 9:3 Exhaust heat frost protection tripped | 0 | 1 |  |  | 2.43
624 | 623 | Active alarm 124 | Alarm 9:4 Exhaust heat frost protection temperature sensor defective | 0 | 1 |  |  | 2.43
625 | 624 | Active alarm 125 | Alarm 9:5 Exhaust heat temperature sensor defective | 0 | 1 |  |  | 2.43
626 | 625 | Active alarm 126 | Alarm 9:6 Exhaust heat valve monitoring tripped | 0 | 1 |  |  | 2.43
627 | 626 | Active alarm 127 | Alarm 9:7 Exhaust heat temperature below set point alarm limit | 0 | 1 |  |  | 2.43
628 | 627 | Active alarm 128 | Alarm 9:8 Exhaust heat alarm input tripped | 0 | 1 |  |  | 2.43
629 | 628 | Active alarm 129 |  | 0 | 1
630 | 629 | Active alarm 130 |  | 0 | 1
631 | 630 | Active alarm 131 |  | 0 | 1
632 | 631 | Active alarm 132 |  | 0 | 1
633 | 632 | Active alarm 133 |  | 0 | 1
634 | 633 | Active alarm 134 |  | 0 | 1
635 | 634 | Active alarm 135 |  | 0 | 1
636 | 635 | Active alarm 136 | Alarm 10:1 Supply air temperature sensor defective | 0 | 1
637 | 636 | Active alarm 137 | Alarm 10:2 Supply air temperature sensor for density compensation defective | 0 | 1
638 | 637 | Active alarm 138 | Alarm 10:3 Extract air temperature sensor defective | 0 | 1
639 | 638 | Active alarm 139 | Alarm 10:4 Extract air temperature sensor for density compensation defective | 0 | 1
640 | 639 | Active alarm 140 | Alarm 10:5 Extract air temperature sensor for heat exchanger defrosting defective | 0 | 1
641 | 640 | Active alarm 141 | Alarm 10:6 Extract air temperature sensor for density compensation in SD air handling unit defective | 0 | 1
642 | 641 | Active alarm 142 | Alarm 10:7 Extract air duct temperature sensor defective | 0 | 1 |  |  | 1.13
643 | 642 | Active alarm 143 |  | 0 | 1
644 | 643 | Active alarm 144 |  | 0 | 1
645 | 644 | Active alarm 145 | Alarm 10:10 Outdoor air temperature sensor defective | 0 | 1
646 | 645 | Active alarm 146 |  | 0 | 1
647 | 646 | Active alarm 147 |  | 0 | 1
648 | 647 | Active alarm 148 |  | 0 | 1
649 | 648 | Active alarm 149 |  | 0 | 1
650 | 649 | Active alarm 150 |  | 0 | 1
651 | 650 | Active alarm 151 | Alarm 11:1 Room temperature sensor no. 1 defective | 0 | 1
652 | 651 | Active alarm 152 | Alarm 11:2 Room temperature sensor no. 2 defective | 0 | 1
653 | 652 | Active alarm 153 | Alarm 11:3 Room temperature sensor no. 3 defective | 0 | 1
654 | 653 | Active alarm 154 | Alarm 11:4 Room temperature sensor no. 4 defective | 0 | 1
655 | 654 | Active alarm 155 | Alarm 11:5 Xzone, room temperature sensor no. 5 defective | 0 | 1
656 | 655 | Active alarm 156 | Alarm 11:6 Xzone, room temperature sensor no. 6 defective | 0 | 1
657 | 656 | Active alarm 157 | Alarm 11:7 Xzone, room temperature sensor no. 7 defective | 0 | 1
658 | 657 | Active alarm 158 | Alarm 11:8 Xzone, room temperature sensor no. 8 defective | 0 | 1
659 | 658 | Active alarm 159 | Alarm 11:9 Outdoor temperature sensor no. A defective | 0 | 1
660 | 659 | Active alarm 160 | Alarm 11:10 Outdoor temperature sensor no. B defective | 0 | 1
661 | 660 | Active alarm 161 | Alarm 11:11 Outdoor temperature sensor no. C defective | 0 | 1
662 | 661 | Active alarm 162 | Alarm 11:12 Outdoor temperature sensor no. D defective | 0 | 1
663 | 662 | Active alarm 163 | Alarm 11:13 Room temperature from communication error | 0 | 1
664 | 663 | Active alarm 164 | Alarm 11:14 Xzone, room temperature from communication error | 0 | 1
665 | 664 | Active alarm 165 | Alarm 11:15 Outdoor temperature from communication error | 0 | 1
666 | 665 | Active alarm 166 | Alarm 12:1 Supply air temperature below set point alarm limit | 0 | 1
667 | 666 | Active alarm 167 | Alarm 12:2 Supply air temperature above set point alarm limit | 0 | 1
668 | 667 | Active alarm 168 |  | 0 | 1
669 | 668 | Active alarm 169 |  | 0 | 1
670 | 669 | Active alarm 170 |  | 0 | 1
671 | 670 | Active alarm 171 | Alarm 12:6 Extract air temperature below alarm limit | 0 | 1
672 | 671 | Active alarm 172 |  | 0 | 1
673 | 672 | Active alarm 173 |  | 0 | 1
674 | 673 | Active alarm 174 |  | 0 | 1
675 | 674 | Active alarm 175 |  | 0 | 1
676 | 675 | Active alarm 176 | Alarm 12:11 temperature guard below Alarm limit | 0 | 1
677 | 676 | Active alarm 177 |  | 0 | 1
678 | 677 | Active alarm 178 | Alarm 12:13 Heat exchange efficiency below alarm limit | 0 | 1 |  |  | 1.21
679 | 678 | Active alarm 179 |  | 0 | 1
680 | 679 | Active alarm 180 |  | 0 | 1
681 | 680 | Active alarm 181 | Alarm 13:1 Humidification, I/O-module no. 4 communication error | 0 | 1
682 | 681 | Active alarm 182 | Alarm 13:2 Supply air humidity sensor defective | 0 | 1
683 | 682 | Active alarm 183 | Alarm 13:3 Extract air humidity sensor defective | 0 | 1
684 | 683 | Active alarm 184 | Alarm 13:4 Exhaust air humidity sensor defective | 0 | 1 |  |  | 1.21
685 | 684 | Active alarm 185 | Alarm 13:5 Outdoor air humidity sensor defective | 0 | 1 |  |  | 2.36
686 | 685 | Active alarm 186 | Alarm 13:6 Room humidity sensor defective | 0 | 1 |  |  | 2.36
687 | 686 | Active alarm 187 |  | 0 | 1
688 | 687 | Active alarm 188 |  | 0 | 1
689 | 688 | Active alarm 189 | Alarm 13:9 Humidifier alarm output tripped | 0 | 1
690 | 689 | Active alarm 190 |  | 0 | 1
691 | 690 | Active alarm 191 | Alarm 13:11 VOC sensor, communication error | 0 | 1
692 | 691 | Active alarm 192 | Alarm 13:12 VOC sensor, internal communication error | 0 | 1
693 | 692 | Active alarm 193 | Alarm 13:13 VOC sensor, internal error | 0 | 1 |  |  | 1.10
694 | 693 | Active alarm 194 | Alarm 13:14 VOC sensor, level below/above set point alarm limit | 0 | 1 |  |  | 1.10
695 | 694 | Active alarm 195 |  | 0 | 1
696 | 695 | Active alarm 196 | Alarm 14:1 Re-heat energy measurement I/O-module no. 6 com. error | 0 | 1 |  |  | 2.47
697 | 696 | Active alarm 197 | Alarm 14:2 Re-heat energy measurement return water temp. sensor defective | 0 | 1 |  |  | 2.47
698 | 697 | Active alarm 198 | Alarm 14:3 Re-heat energy measurement feed water temp. sensor defective | 0 | 1 |  |  | 2.47
699 | 698 | Active alarm 199 | Alarm 14:4 Re-heat energy measurement valve leakage | 0 | 1 |  |  | 2.47
700 | 699 | Active alarm 200 | Alarm 14:5 Re-heat energy measurement flow sensor defective | 0 | 1 |  |  | 2.47
701 | 700 | Active alarm 201 |  | 0 | 1 |  |  | 2.47
702 | 701 | Active alarm 202 |  | 0 | 1 |  |  | 2.47
703 | 702 | Active alarm 203 | Alarm 14:8 Cool energy measurement I/O-module no. 7 com. error | 0 | 1 |  |  | 2.47
704 | 703 | Active alarm 204 | Alarm 14:9 Cool energy measurement return water temp. sensor defective | 0 | 1 |  |  | 2.47
705 | 704 | Active alarm 205 | Alarm 14:10 Cool energy measurement feed water temp. sensor defective | 0 | 1 |  |  | 2.47
706 | 705 | Active alarm 206 | Alarm 14:11 Cool energy measurement valve leakage | 0 | 1 |  |  | 2.47
707 | 706 | Active alarm 207 | Alarm 14:12 Cool energy measurement flow sensor defective | 0 | 1 |  |  | 2.47
708 | 707 | Active alarm 208 |  | 0 | 1
709 | 708 | Active alarm 209 |  | 0 | 1
710 | 709 | Active alarm 210 |  | 0 | 1
711 | 710 | Active alarm 211 | Alarm 15:1 Plate heat exchanger, I/O-module no. 2 communication error | 0 | 1
712 | 711 | Active alarm 212 | Alarm 15:2 Plate heat exchanger, temperature sensor no. 1 defective | 0 | 1
713 | 712 | Active alarm 213 | Alarm 15:3 Plate heat exchanger, temperature sensor no. 2 defective | 0 | 1
714 | 713 | Active alarm 214 | Alarm 15:4 Plate heat exchanger, damper monitor tripped | 0 | 1
715 | 714 | Active alarm 215 |  | 0 | 1
716 | 715 | Active alarm 216 | Alarm 15:6 Plate heat exchanger bypass damper 4A monitor tripped | 0 | 1 |  |  | 2.43
717 | 716 | Active alarm 217 | Alarm 15:7 Plate heat exchanger, I/O-module no. 3 communication error | 0 | 1 |  |  | 1.13
718 | 717 | Active alarm 218 | Alarm 15:8 Plate heat exchanger, bypass damper monitor tripped | 0 | 1 |  |  | 1.13
719 | 718 | Active alarm 219 | Alarm 15:9 Plate heat exchanger, damper no. 1 monitor tripped | 0 | 1 |  |  | 1.13
720 | 719 | Active alarm 220 | Alarm 15:10 Plate heat exchanger, damper no. 2 monitor tripped | 0 | 1 |  |  | 1.13
721 | 720 | Active alarm 221 | Alarm 15:11 Plate heat exchanger, I/O-module no. 3 communication error | 0 | 1 |  |  | 1.13
722 | 721 | Active alarm 222 | Alarm 15:12 Plate heat exchanger, bypass damper monitor tripped | 0 | 1 |  |  | 1.13
723 | 722 | Active alarm 223 | Alarm 15:13 Plate counter flow heat exchanger, defrost pressure above alarm limit | 0 | 1 |  |  | 1.21
724 | 723 | Active alarm 224 | Alarm 15:14 Plate heat exchanger, defrost pressure sensor no. C communication error | 0 | 1 |  |  | 1.13
725 | 724 | Active alarm 225 | Alarm 15:15 Plate heat exchanger, defrost pressure above alarm limit | 0 | 1 |  |  | 1.13
726 | 725 | Active alarm 226 | Alarm 16:1 Coil heat exchanger, I/O-module no. 1 communication error | 0 | 1
727 | 726 | Active alarm 227 | Alarm 16:2 Coil heat exchanger, temperature sensor defective | 0 | 1
728 | 727 | Active alarm 228 | Alarm 16:3 Coil heat exchanger, valve monitor tripped | 0 | 1
729 | 728 | Active alarm 229 | Alarm 16:4 Coil heat exchanger, pump monitor tripped | 0 | 1
730 | 729 | Active alarm 230 | Alarm 16:5 Coil heat exchanger, I/O-module no. C communication error | 0 | 1 |  |  | 1.18
731 | 730 | Active alarm 231 | Alarm 16:6 Coil heat exchanger, pressure sensor defective | 0 | 1 |  |  | 1.18
732 | 731 | Active alarm 232 | Alarm 16:7 Coil heat exchanger, low pressure brine circuit | 0 | 1 |  |  | 1.18
733 | 732 | Active alarm 233 | Alarm 16:8 Coil heat exchanger pressure below alarm limit | 0 | 1 |  |  | 1.27
734 | 733 | Active alarm 234 |  | 0 | 1
735 | 734 | Active alarm 235 |  | 0 | 1
736 | 735 | Active alarm 236 |  | 0 | 1
737 | 736 | Active alarm 237 |  | 0 | 1
738 | 737 | Active alarm 238 |  | 0 | 1
739 | 738 | Active alarm 239 |  | 0 | 1
740 | 739 | Active alarm 240 |  | 0 | 1
741 | 740 | Active alarm 241 | Alarm 17:1 Rotary heat exchanger, motor controller communication error | 0 | 1
742 | 741 | Active alarm 242 | Alarm 17:2 Rotary heat exchanger, defrost pressure sensor no. 7 communication error | 0 | 1
743 | 742 | Active alarm 243 | Alarm 17:3 Rotary heat exchanger, defrost pressure above alarm limit | 0 | 1
744 | 743 | Active alarm 244 | Alarm 17:4 Rotary heat exchanger, speed monitor tripped | 0 | 1
745 | 744 | Active alarm 245 | Alarm 17:5 Rotary heat exchanger, motor controller over current | 0 | 1
746 | 745 | Active alarm 246 | Alarm 17:6 Rotary heat exchanger, motor controller under voltage | 0 | 1
747 | 746 | Active alarm 247 | Alarm 17:7 Rotary heat exchanger, motor controller over voltage | 0 | 1
748 | 747 | Active alarm 248 | Alarm 17:8 Rotary heat exchanger, motor controller over temperature | 0 | 1
749 | 748 | Active alarm 249 | Alarm 17:9 Rotary heat exchanger, motor controller start error | 0 | 1
750 | 749 | Active alarm 250 | Alarm 17:10 Rotary heat exchanger, motor controller internal error | 0 | 1 |  |  | 1.32
751 | 750 | Active alarm 251 | Alarm 17:11 Rotary heat exchanger, motor controller phase error | 0 | 1 |  |  | 1.32
752 | 751 | Active alarm 252 | Alarm 17:12 Rotary heat exchanger, motor controller internal memory error | 0 | 1 |  |  | 1.32
753 | 752 | Active alarm 253 | Alarm 17:13 Rotary heat exchanger, motor controller current reduction | 0 | 1 |  |  | 1.32
754 | 753 | Active alarm 254 | Alarm 17:14 Rotary heat exchanger, motor controller internal com. error | 0 | 1 |  |  | 1.32
755 | 754 | Active alarm 255 | Alarm 17:15 Rotary heat exchanger, I/O-module com. error | 0 | 1 |  |  | 1.32
756 | 755 | Active alarm 256 | Alarm 18:1 AYC, I/O-module no. 7 communication error | 0 | 1
757 | 756 | Active alarm 257 | Alarm 18:2 AYC heat, temperature sensor defective | 0 | 1
758 | 757 | Active alarm 258 | Alarm 18:3 AYC heat, valve monitor tripped | 0 | 1
759 | 758 | Active alarm 259 | Alarm 18:4 AYC heat, pump monitor tripped | 0 | 1
760 | 759 | Active alarm 260 | Alarm 18:5 AYC heat, temperature below set point alarm limit | 0 | 1
761 | 760 | Active alarm 261 | Alarm 18:6 AYC heat, temperature above set point alarm limit | 0 | 1
762 | 761 | Active alarm 262 |  | 0 | 1
763 | 762 | Active alarm 263 |  | 0 | 1
764 | 763 | Active alarm 264 | Alarm 18:9 AYC cool, temperature sensor defective | 0 | 1
765 | 764 | Active alarm 265 | Alarm 18:10 AYC cool, valve monitor tripped | 0 | 1
766 | 765 | Active alarm 266 | Alarm 18:11 AYC cool, pump monitor tripped | 0 | 1
767 | 766 | Active alarm 267 | Alarm 18:12 AYC cool, temperature below set point alarm limit | 0 | 1
768 | 767 | Active alarm 268 | Alarm 18:13 AYC cool, temperature above set point alarm limit | 0 | 1
769 | 768 | Active alarm 269 |  | 0 | 1
770 | 769 | Active alarm 270 |  | 0 | 1
771 | 770 | Active alarm 271 | Alarm 19:1 Rotary heat exchanger, AQC pressure sensor no. E com. error | 0 | 1 |  |  | 1.32
772 | 771 | Active alarm 272 | Alarm 19:2 Rotary heat exchanger, AQC pressure below set point alarm limit | 0 | 1 |  |  | 1.32
773 | 772 | Active alarm 273 | Alarm 19:3 Rotary heat exchanger, AQC damper monitoring tripped | 0 | 1 |  |  | 1.32
774 | 773 | Active alarm 274 |  | 0 | 1
775 | 774 | Active alarm 275 |  | 0 | 1
776 | 775 | Active alarm 276 |  | 0 | 1
777 | 776 | Active alarm 277 |  | 0 | 1
778 | 777 | Active alarm 278 |  | 0 | 1
779 | 778 | Active alarm 279 |  | 0 | 1
780 | 779 | Active alarm 280 |  | 0 | 1
781 | 780 | Active alarm 281 |  | 0 | 1
782 | 781 | Active alarm 282 |  | 0 | 1
783 | 782 | Active alarm 283 |  | 0 | 1
784 | 783 | Active alarm 284 |  | 0 | 1
785 | 784 | Active alarm 285 |  | 0 | 1
786 | 785 | Active alarm 286 |  | 0 | 1
787 | 786 | Active alarm 287 |  | 0 | 1
788 | 787 | Active alarm 288 |  | 0 | 1
789 | 788 | Active alarm 289 |  | 0 | 1
790 | 789 | Active alarm 290 |  | 0 | 1
791 | 790 | Active alarm 291 |  | 0 | 1
792 | 791 | Active alarm 292 |  | 0 | 1
793 | 792 | Active alarm 293 |  | 0 | 1
794 | 793 | Active alarm 294 |  | 0 | 1
795 | 794 | Active alarm 295 |  | 0 | 1
796 | 795 | Active alarm 296 |  | 0 | 1
797 | 796 | Active alarm 297 |  | 0 | 1
798 | 797 | Active alarm 298 |  | 0 | 1
799 | 798 | Active alarm 299 |  | 0 | 1
800 | 799 | Active alarm 300 |  | 0 | 1
801 | 800 | Active alarm 301 | Alarm 21:1 COOL DX, I/O-module no. 2 communication error | 0 | 1
802 | 801 | Active alarm 302 | Alarm 21:2 COOL DX, compressor no. 1 low pressure sensor defective | 0 | 1
803 | 802 | Active alarm 303 | Alarm 21:3 COOL DX, compressor no. 1 low pressure below alarm limit | 0 | 1
804 | 803 | Active alarm 304 | Alarm 21:4 COOL DX, compressor no. 1 high pressure sensor defective | 0 | 1
805 | 804 | Active alarm 305 | Alarm 21:5 COOL DX, compressor no. 1 high pressure above alarm limit | 0 | 1
806 | 805 | Active alarm 306 | Alarm 21:6 COOL DX, compressor no. 1 monitor tripped | 0 | 1
807 | 806 | Active alarm 307 | Alarm 21:7 COOL DX, compressor no. 1 restart error | 0 | 1
808 | 807 | Active alarm 308 | Alarm 21:8 COOL DX, compressor no. 2 low pressure sensor defective | 0 | 1
809 | 808 | Active alarm 309 | Alarm 21:9 COOL DX, compressor no. 2 low pressure below alarm limit | 0 | 1
810 | 809 | Active alarm 310 | Alarm 21:10 COOL DX, compressor no. 2 high pressure sensor defective | 0 | 1
811 | 810 | Active alarm 311 | Alarm 21:11 COOL DX, compressor no. 2 high pressure above alarm limit | 0 | 1
812 | 811 | Active alarm 312 | Alarm 21:12 COOL DX, compressor no. 2 monitor tripped | 0 | 1
813 | 812 | Active alarm 313 | Alarm 21:13 COOL DX, compressor no. 2 restart error | 0 | 1
814 | 813 | Active alarm 314 | Alarm 21:14 COOL DX, outdoor air temperature sensor defective | 0 | 1
815 | 814 | Active alarm 315 | Alarm 21:15 COOL DX phase sequence error or supply voltage missing | 0 | 1
816 | 815 | Active alarm 316 | Alarm 22:1 Xzone heat energy measurement I/O-module no. D com. error | 0 | 1 |  |  | 2.47
817 | 816 | Active alarm 317 | Alarm 22:2 Xzone heat energy measurement return water temp. sensor defective | 0 | 1 |  |  | 2.47
818 | 817 | Active alarm 318 | Alarm 22:3 Xzone heat energy measurement feed water temp. sensor defective | 0 | 1 |  |  | 2.47
819 | 818 | Active alarm 319 | Alarm 22:4 Xzone heat energy measurement valve leakage | 0 | 1 |  |  | 2.47
820 | 819 | Active alarm 320 | Alarm 22:5 Xzone heat energy measurement flow sensor defective | 0 | 1 |  |  | 2.47
821 | 820 | Active alarm 321 |  | 0 | 1 |  |  | 2.47
822 | 821 | Active alarm 322 |  | 0 | 1 |  |  | 2.47
823 | 822 | Active alarm 323 | Alarm 22:8 Xzone cool energy measurement I/O-module no. E com. error | 0 | 1 |  |  | 2.47
824 | 823 | Active alarm 324 | Alarm 22:9 Xzone cool energy measurement return water temp. sensor defective | 0 | 1 |  |  | 2.47
825 | 824 | Active alarm 325 | Alarm 22:10 Xzone cool energy measurement feed water temp. sensor defective | 0 | 1 |  |  | 2.47
826 | 825 | Active alarm 326 | Alarm 22:11 Xzone cool energy measurement valve leakage | 0 | 1 |  |  | 2.47
827 | 826 | Active alarm 327 | Alarm 22:12 Xzone cool energy measurement flow sensor defective | 0 | 1 |  |  | 2.47
828 | 827 | Active alarm 328 |  | 0 | 1
829 | 828 | Active alarm 329 |  | 0 | 1
830 | 829 | Active alarm 330 |  | 0 | 1
831 | 830 | Active alarm 331 | Alarm 23:1 SMART Link, communication error | 0 | 1
832 | 831 | Active alarm 332 | Alarm 23:2 SMART Link, alarm level 1 tripped | 0 | 1
833 | 832 | Active alarm 333 | Alarm 23:3 SMART Link, alarm level 2 tripped | 0 | 1
834 | 833 | Active alarm 334 | Alarm 23:4 SMART Link, alarm level 3 tripped | 0 | 1
835 | 834 | Active alarm 335 |  | 0 | 1
836 | 835 | Active alarm 336 |  | 0 | 1
837 | 836 | Active alarm 337 |  | 0 | 1
838 | 837 | Active alarm 338 |  | 0 | 1
839 | 838 | Active alarm 339 |  | 0 | 1
840 | 839 | Active alarm 340 | Alarm 23:10 AQUA Link, I/O-module no. 5 communication error | 0 | 1
841 | 840 | Active alarm 341 | Alarm 23:11 AQUA Link, pump monitor tripped | 0 | 1
842 | 841 | Active alarm 342 |  | 0 | 1
843 | 842 | Active alarm 343 |  | 0 | 1
844 | 843 | Active alarm 344 |  | 0 | 1
845 | 844 | Active alarm 345 |  | 0 | 1
846 | 845 | Active alarm 346 | Alarm 24:1 SMART Link, no. 1 communication error | 0 | 1
847 | 846 | Active alarm 347 | Alarm 24:2 SMART Link, no. 1 alarm tripped | 0 | 1
848 | 847 | Active alarm 348 |  | 0 | 1
849 | 848 | Active alarm 349 | Alarm 24:4 SMART Link, no. 2 communication error | 0 | 1
850 | 849 | Active alarm 350 | Alarm 24:5 SMART Link, no. 2 alarm tripped | 0 | 1
851 | 850 | Active alarm 351 |  | 0 | 1
852 | 851 | Active alarm 352 | Alarm 24:7 SMART Link, no. 3 communication error | 0 | 1
853 | 852 | Active alarm 353 | Alarm 24:8 SMART Link, no. 3 alarm tripped | 0 | 1
854 | 853 | Active alarm 354 |  | 0 | 1
855 | 854 | Active alarm 355 | Alarm 24:10 SMART Link, no. 4 communication error | 0 | 1
856 | 855 | Active alarm 356 | Alarm 24:11 SMART Link, no. 4 alarm tripped | 0 | 1
857 | 856 | Active alarm 357 |  | 0 | 1
858 | 857 | Active alarm 358 | Alarm 24:13 SMART Link supply air flow below alarm limit | 0 | 1 |  |  | 1.25
859 | 858 | Active alarm 359 |  | 0 | 1
860 | 859 | Active alarm 360 |  | 0 | 1
861 | 860 | Active alarm 361 | Alarm 25:1 SMART Link+, cooling circuit A com. error | 0 | 1 |  |  | 1.32
862 | 861 | Active alarm 362 | Alarm 25:2 SMART Link+, cooling circuit B com. error | 0 | 1 |  |  | 1.32
863 | 862 | Active alarm 363 | Alarm 25:3 SMART Link+, heating circuit A com. error | 0 | 1 |  |  | 1.32
864 | 863 | Active alarm 364 | Alarm 25:4 SMART Link+, heating circuit B com. error | 0 | 1 |  |  | 1.32
865 | 864 | Active alarm 365 |  | 0 | 1
866 | 865 | Active alarm 366 |  | 0 | 1
867 | 866 | Active alarm 367 |  | 0 | 1
868 | 867 | Active alarm 368 |  | 0 | 1
869 | 868 | Active alarm 369 |  | 0 | 1
870 | 869 | Active alarm 370 |  | 0 | 1
871 | 870 | Active alarm 371 |  | 0 | 1
872 | 871 | Active alarm 372 |  | 0 | 1
873 | 872 | Active alarm 373 |  | 0 | 1
874 | 873 | Active alarm 374 |  | 0 | 1
875 | 874 | Active alarm 375 |  | 0 | 1
876 | 875 | Active alarm 376 | Alarm 26:1 Pre-filter, supply air pressure sensor no.8 communication error | 0 | 1
877 | 876 | Active alarm 377 | Alarm 26:2 Pre-filter, supply air dirty | 0 | 1
878 | 877 | Active alarm 378 |  | 0 | 1
879 | 878 | Active alarm 379 |  | 0 | 1
880 | 879 | Active alarm 380 |  | 0 | 1
881 | 880 | Active alarm 381 |  | 0 | 1
882 | 881 | Active alarm 382 | Alarm 26:7 Pre-filter, extract air pressure sensor no.9 communication error | 0 | 1
883 | 882 | Active alarm 383 | Alarm 26:8 Pre-filter, extract air dirty | 0 | 1
884 | 883 | Active alarm 384 |  | 0 | 1
885 | 884 | Active alarm 385 |  | 0 | 1
886 | 885 | Active alarm 386 |  | 0 | 1
887 | 886 | Active alarm 387 |  | 0 | 1
888 | 887 | Active alarm 388 |  | 0 | 1
889 | 888 | Active alarm 389 |  | 0 | 1
890 | 889 | Active alarm 390 |  | 0 | 1
891 | 890 | Active alarm 391 | Alarm 27:1 Air handling unit filter, supply air pressure sensor no. 3/4 communication error | 0 | 1
892 | 891 | Active alarm 392 | Alarm 27:2 Air handling unit filter, supply air dirty | 0 | 1
893 | 892 | Active alarm 393 |  | 0 | 1
894 | 893 | Active alarm 394 |  | 0 | 1
895 | 894 | Active alarm 395 |  | 0 | 1
896 | 895 | Active alarm 396 |  | 0 | 1
897 | 896 | Active alarm 397 | Alarm 27:7 Air handling unit filter, extract air pressure sensor no. 3/4 communication error | 0 | 1
898 | 897 | Active alarm 398 | Alarm 27:8 Air handling unit filter, extract air dirty | 0 | 1
899 | 898 | Active alarm 399 |  | 0 | 1
900 | 899 | Active alarm 400 |  | 0 | 1
901 | 900 | Active alarm 401 |  | 0 | 1
902 | 901 | Active alarm 402 |  | 0 | 1
903 | 902 | Active alarm 403 |  | 0 | 1
904 | 903 | Active alarm 404 |  | 0 | 1
905 | 904 | Active alarm 405 |  | 0 | 1
906 | 905 | Active alarm 406 | Alarm 28:1 End filter, supply air pressure sensor no. A communication error | 0 | 1
907 | 906 | Active alarm 407 | Alarm 28:2 End filter, supply air dirty | 0 | 1
908 | 907 | Active alarm 408 |  | 0 | 1
909 | 908 | Active alarm 409 |  | 0 | 1
910 | 909 | Active alarm 410 |  | 0 | 1
911 | 910 | Active alarm 411 |  | 0 | 1
912 | 911 | Active alarm 412 |  | 0 | 1
913 | 912 | Active alarm 413 |  | 0 | 1
914 | 913 | Active alarm 414 |  | 0 | 1
915 | 914 | Active alarm 415 |  | 0 | 1
916 | 915 | Active alarm 416 |  | 0 | 1
917 | 916 | Active alarm 417 |  | 0 | 1
918 | 917 | Active alarm 418 |  | 0 | 1
919 | 918 | Active alarm 419 |  | 0 | 1
920 | 919 | Active alarm 420 |  | 0 | 1
921 | 920 | Active alarm 421 | Alarm 29:1 Energy monitoring pulse counter com. Error | 0 | 1 |  |  | 2.42
922 | 921 | Active alarm 422 |  | 0 | 1
923 | 922 | Active alarm 423 |  | 0 | 1
924 | 923 | Active alarm 424 |  | 0 | 1
925 | 924 | Active alarm 425 |  | 0 | 1
926 | 925 | Active alarm 426 |  | 0 | 1
927 | 926 | Active alarm 427 |  | 0 | 1
928 | 927 | Active alarm 428 |  | 0 | 1
929 | 928 | Active alarm 429 |  | 0 | 1
930 | 929 | Active alarm 430 |  | 0 | 1
931 | 930 | Active alarm 431 |  | 0 | 1
932 | 931 | Active alarm 432 |  | 0 | 1
933 | 932 | Active alarm 433 |  | 0 | 1
934 | 933 | Active alarm 434 |  | 0 | 1
935 | 934 | Active alarm 435 |  | 0 | 1
936 | 935 | Active alarm 436 | Alarm 30:1 Air flow measurement, supply air pressure sensor no. 1/2 communication error | 0 | 1
937 | 936 | Active alarm 437 | Alarm 30:2 Air flow measurement, supply air flow below set point alarm limit | 0 | 1
938 | 937 | Active alarm 438 | Alarm 30:3 Air flow measurement, supply air flow above set point alarm limit | 0 | 1
939 | 938 | Active alarm 439 |  | 0 | 1
940 | 939 | Active alarm 440 |  | 0 | 1
941 | 940 | Active alarm 441 | Alarm 30:6 Air flow measurement, extract air pressure sensor no. 1/2 communication error | 0 | 1
942 | 941 | Active alarm 442 | Alarm 30:7 Air flow measurement, extract air flow below set point alarm limit | 0 | 1
943 | 942 | Active alarm 443 | Alarm 30:8 Air flow measurement, extract air flow above set point alarm limit | 0 | 1
944 | 943 | Active alarm 444 |  | 0 | 1
945 | 944 | Active alarm 445 |  | 0 | 1
946 | 945 | Active alarm 446 | Alarm 30:11 Air flow measurement, carry over control pressure sensor no. B communication error | 0 | 1
947 | 946 | Active alarm 447 |  | 0 | 1
948 | 947 | Active alarm 448 |  | 0 | 1
949 | 948 | Active alarm 449 |  | 0 | 1
950 | 949 | Active alarm 450 |  | 0 | 1
951 | 950 | Active alarm 451 | Alarm 31:1 Pressure regulation, supply air pressure sensor no. 5 communication error | 0 | 1
952 | 951 | Active alarm 452 | Alarm 31:2 Pressure regulation, supply air pressure below set point alarm limit | 0 | 1
953 | 952 | Active alarm 453 | Alarm 31:3 Pressure regulation, supply air pressure above set point alarm limit | 0 | 1
954 | 953 | Active alarm 454 |  | 0 | 1
955 | 954 | Active alarm 455 |  | 0 | 1
956 | 955 | Active alarm 456 | Alarm 31:6 Pressure regulation, extract air pressure sensor no. 6 communication error | 0 | 1
957 | 956 | Active alarm 457 | Alarm 31:7 Pressure regulation, extract air pressure below set point alarm limit | 0 | 1
958 | 957 | Active alarm 458 | Alarm 31:8 Pressure regulation, extract air pressure above set point alarm limit | 0 | 1
959 | 958 | Active alarm 459 |  | 0 | 1
960 | 959 | Active alarm 460 |  | 0 | 1
961 | 960 | Active alarm 461 |  | 0 | 1
962 | 961 | Active alarm 462 |  | 0 | 1
963 | 962 | Active alarm 463 |  | 0 | 1
964 | 963 | Active alarm 464 |  | 0 | 1
965 | 964 | Active alarm 465 |  | 0 | 1
966 | 965 | Active alarm 466 | Alarm 32:1 ReCO2, I/O-module no. 0 communication error | 0 | 1
967 | 966 | Active alarm 467 | Alarm 32:2 ReCO2, pressure sensor no. 0 communication error | 0 | 1
968 | 967 | Active alarm 468 | Alarm 32:3 ReCO2, recirculation damper monitoring tripped | 0 | 1
969 | 968 | Active alarm 469 | Alarm 32:4 ReCO2, outdoor air damper monitoring tripped | 0 | 1
970 | 969 | Active alarm 470 |  | 0 | 1
971 | 970 | Active alarm 471 |  | 0 | 1
972 | 971 | Active alarm 472 |  | 0 | 1
973 | 972 | Active alarm 473 |  | 0 | 1
974 | 973 | Active alarm 474 |  | 0 | 1
975 | 974 | Active alarm 475 |  | 0 | 1
976 | 975 | Active alarm 476 |  | 0 | 1
977 | 976 | Active alarm 477 |  | 0 | 1
978 | 977 | Active alarm 478 |  | 0 | 1
979 | 978 | Active alarm 479 |  | 0 | 1
980 | 979 | Active alarm 480 |  | 0 | 1
981 | 980 | Active alarm 481 | Alarm 33:1 Service period above alarm limit | 0 | 1
982 | 981 | Active alarm 482 |  | 0 | 1
983 | 982 | Active alarm 483 |  | 0 | 1
984 | 983 | Active alarm 484 |  | 0 | 1
985 | 984 | Active alarm 485 |  | 0 | 1
986 | 985 | Active alarm 486 |  | 0 | 1
987 | 986 | Active alarm 487 |  | 0 | 1
988 | 987 | Active alarm 488 |  | 0 | 1
989 | 988 | Active alarm 489 |  | 0 | 1
990 | 989 | Active alarm 490 |  | 0 | 1
991 | 990 | Active alarm 491 |  | 0 | 1
992 | 991 | Active alarm 492 |  | 0 | 1
993 | 992 | Active alarm 493 |  | 0 | 1
994 | 993 | Active alarm 494 |  | 0 | 1
995 | 994 | Active alarm 495 | Alarm 33:15 Lock function tripped | 0 | 1
996 | 995 | Active alarm 496 | Alarm 34:1 External control I/O-module no. 3 communication error | 0 | 1
997 | 996 | Active alarm 497 | Alarm 34:2 External control I/O-module no. 6 communication error | 0 | 1
998 | 997 | Active alarm 498 |  | 0 | 1
999 | 998 | Active alarm 499 |  | 0 | 1
1000 | 999 | Active alarm 500 |  | 0 | 1
1001 | 1000 | Active alarm 501 |  | 0 | 1
1002 | 1001 | Active alarm 502 |  | 0 | 1
1003 | 1002 | Active alarm 503 |  | 0 | 1
1004 | 1003 | Active alarm 504 |  | 0 | 1
1005 | 1004 | Active alarm 505 |  | 0 | 1
1006 | 1005 | Active alarm 506 |  | 0 | 1
1007 | 1006 | Active alarm 507 |  | 0 | 1
1008 | 1007 | Active alarm 508 |  | 0 | 1
1009 | 1008 | Active alarm 509 |  | 0 | 1
1010 | 1009 | Active alarm 510 |  | 0 | 1
1011 | 1010 | Active alarm 511 | Alarm 35:1 Booster diffusers, I/O-module no. 8 communication error | 0 | 1
1012 | 1011 | Active alarm 512 |  | 0 | 1
1013 | 1012 | Active alarm 513 |  | 0 | 1
1014 | 1013 | Active alarm 514 |  | 0 | 1
1015 | 1014 | Active alarm 515 |  | 0 | 1
1016 | 1015 | Active alarm 516 |  | 0 | 1
1017 | 1016 | Active alarm 517 |  | 0 | 1
1018 | 1017 | Active alarm 518 |  | 0 | 1
1019 | 1018 | Active alarm 519 |  | 0 | 1
1020 | 1019 | Active alarm 520 |  | 0 | 1
1021 | 1020 | Active alarm 521 |  | 0 | 1
1022 | 1021 | Active alarm 522 |  | 0 | 1
1023 | 1022 | Active alarm 523 |  | 0 | 1
1024 | 1023 | Active alarm 524 |  | 0 | 1
1025 | 1024 | Active alarm 525 |  | 0 | 1
1026 | 1025 | Active alarm 526 | Alarm 36:1 External BMS control I/O-module no. A communication error | 0 | 1 |  |  | 1.20
1027 | 1026 | Active alarm 527 | Alarm 36:2 External BMS control I/O-module no. A temperature sensor no. 1 defective | 0 | 1 |  |  | 1.20
1028 | 1027 | Active alarm 528 | Alarm 36:3 External BMS control I/O-module no. A temperature sensor no. 2 defective | 0 | 1 |  |  | 1.20
1029 | 1028 | Active alarm 529 |  | 0 | 1 |  |  | 1.20
1030 | 1029 | Active alarm 530 |  | 0 | 1 |  |  | 1.20
1031 | 1030 | Active alarm 531 | Alarm 36:6 External BMS control I/O-module no. B communication error | 0 | 1 |  |  | 1.20
1032 | 1031 | Active alarm 532 | Alarm 36:7 External BMS control I/O-module no. B temperature sensor no. 1 defective | 0 | 1 |  |  | 1.20
1033 | 1032 | Active alarm 533 | Alarm 36:8 External BMS control I/O-module no. B temperature sensor no. 2 defective | 0 | 1 |  |  | 1.20
1034 | 1033 | Active alarm 534 |  | 0 | 1 |  |  | 1.20
1035 | 1034 | Active alarm 535 |  | 0 | 1 |  |  | 1.20
1036 | 1035 | Active alarm 536 | Alarm 36:11 External BMS control I/O-module no. C communication error | 0 | 1 |  |  | 1.20
1037 | 1036 | Active alarm 537 | Alarm 36:12 External BMS control I/O-module no. C temperature sensor no. 1 defective | 0 | 1 |  |  | 1.20
1038 | 1037 | Active alarm 538 | Alarm 36:13 External BMS control I/O-module no. C temperature sensor no. 2 defective | 0 | 1 |  |  | 1.20
1039 | 1038 | Active alarm 539 |  | 0 | 1
1040 | 1039 | Active alarm 540 |  | 0 | 1
1041 | 1040 | Active alarm 541 |  | 0 | 1
1042 | 1041 | Active alarm 542 |  | 0 | 1
1043 | 1042 | Active alarm 543 |  | 0 | 1
1044 | 1043 | Active alarm 544 |  | 0 | 1
1045 | 1044 | Active alarm 545 |  | 0 | 1
1046 | 1045 | Active alarm 546 |  | 0 | 1
1047 | 1046 | Active alarm 547 |  | 0 | 1
1048 | 1047 | Active alarm 548 |  | 0 | 1
1049 | 1048 | Active alarm 549 |  | 0 | 1
1050 | 1049 | Active alarm 550 |  | 0 | 1
1051 | 1050 | Active alarm 551 |  | 0 | 1
1052 | 1051 | Active alarm 552 |  | 0 | 1
1053 | 1052 | Active alarm 553 |  | 0 | 1
1054 | 1053 | Active alarm 554 |  | 0 | 1
1055 | 1054 | Active alarm 555 |  | 0 | 1
1056 | 1055 | Active alarm 556 | Alarm 38:1 MIRU Control no. 1 communication error | 0 | 1
1057 | 1056 | Active alarm 557 | Alarm 38:2 MIRU Control no. 1 motor controller alarm tripped | 0 | 1
1058 | 1057 | Active alarm 558 | Alarm 38:3 MIRU Control no. 1 motor controller communication error | 0 | 1
1059 | 1058 | Active alarm 559 | Alarm 38:4 MIRU Control no. 1 air flow pressure sensor no. 0 communication error | 0 | 1
1060 | 1059 | Active alarm 560 | Alarm 38:5 MIRU Control no. 1 pressure regulation sensor no. 1 communication error | 0 | 1
1061 | 1060 | Active alarm 561 | Alarm 38:6 MIRU Control no. 1 temperature sensor defective | 0 | 1
1062 | 1061 | Active alarm 562 | Alarm 38:7 MIRU Control no. 1 air flow/pressure set point deviation from alarm limit | 0 | 1
1063 | 1062 | Active alarm 563 | Alarm 38:8 MIRU 1 air flow below set point alarm limit | 0 | 1 |  |  | 1.25
1064 | 1063 | Active alarm 564 | Alarm 38:9 MIRU 1 air flow above set point alarm limit | 0 | 1 |  |  | 1.25
1065 | 1064 | Active alarm 565 | Alarm 38:10 MIRU 1 pressure below set point alarm limit | 0 | 1 |  |  | 1.25
1066 | 1065 | Active alarm 566 | Alarm 38:11 MIRU 1 pressure above set point alarm limit | 0 | 1 |  |  | 1.25
1067 | 1066 | Active alarm 567 |  | 0 | 1
1068 | 1067 | Active alarm 568 |  | 0 | 1
1069 | 1068 | Active alarm 569 |  | 0 | 1
1070 | 1069 | Active alarm 570 |  | 0 | 1
1071 | 1070 | Active alarm 571 | Alarm 39:1 MIRU Control no. 2 communication error | 0 | 1
1072 | 1071 | Active alarm 572 | Alarm 39:2 MIRU Control no. 2 motor controller alarm tripped | 0 | 1
1073 | 1072 | Active alarm 573 | Alarm 39:3 MIRU Control no. 2 motor controller communication error | 0 | 1
1074 | 1073 | Active alarm 574 | Alarm 39:4 MIRU Control no. 2 air flow pressure sensor no. 0 communication error | 0 | 1
1075 | 1074 | Active alarm 575 | Alarm 39:5 MIRU Control no. 2 pressure regulation sensor no. 1 communication error | 0 | 1
1076 | 1075 | Active alarm 576 | Alarm 39:6 MIRU Control no. 2 temperature sensor defective | 0 | 1
1077 | 1076 | Active alarm 577 | Alarm 39:7 MIRU Control no. 2 air flow/pressure set point deviation from alarm limit | 0 | 1
1078 | 1077 | Active alarm 578 | Alarm 39:8 MIRU 2 air flow below set point alarm limit | 0 | 1 |  |  | 1.25
1079 | 1078 | Active alarm 579 | Alarm 39:9 MIRU 2 air flow above set point alarm limit | 0 | 1 |  |  | 1.25
1080 | 1079 | Active alarm 580 | Alarm 39:10 MIRU 2 pressure below set point alarm limit | 0 | 1 |  |  | 1.25
1081 | 1080 | Active alarm 581 | Alarm 39:11 MIRU 2 pressure above set point alarm limit | 0 | 1 |  |  | 1.25
1082 | 1081 | Active alarm 582 |  | 0 | 1
1083 | 1082 | Active alarm 583 |  | 0 | 1
1084 | 1083 | Active alarm 584 |  | 0 | 1
1085 | 1084 | Active alarm 585 |  | 0 | 1
1086 | 1085 | Active alarm 586 | Alarm 40:1 MIRU Control no. 3 communication error | 0 | 1
1087 | 1086 | Active alarm 587 | Alarm 40:2 MIRU Control no. 3 motor controller alarm tripped | 0 | 1
1088 | 1087 | Active alarm 588 | Alarm 40:3 MIRU Control no. 3 motor controller communication error | 0 | 1
1089 | 1088 | Active alarm 589 | Alarm 40:4 MIRU Control no. 3 air flow pressure sensor no. 0 communication error | 0 | 1
1090 | 1089 | Active alarm 590 | Alarm 40:5 MIRU Control no. 3 pressure regulation sensor no. 1 communication error | 0 | 1
1091 | 1090 | Active alarm 591 | Alarm 40:6 MIRU Control no. 3 temperature sensor defective | 0 | 1
1092 | 1091 | Active alarm 592 | Alarm 40:7 MIRU Control no. 3 air flow/pressure set point deviation from alarm limit | 0 | 1
1093 | 1092 | Active alarm 593 | Alarm 40:8 MIRU 3 air flow below set point alarm limit | 0 | 1 |  |  | 1.25
1094 | 1093 | Active alarm 594 | Alarm 40:9 MIRU 3 air flow above set point alarm limit | 0 | 1 |  |  | 1.25
1095 | 1094 | Active alarm 595 | Alarm 40:10 MIRU 3 pressure below set point alarm limit | 0 | 1 |  |  | 1.25
1096 | 1095 | Active alarm 596 | Alarm 40:11 MIRU 3 pressure above set point alarm limit | 0 | 1 |  |  | 1.25
1097 | 1096 | Active alarm 597 |  | 0 | 1
1098 | 1097 | Active alarm 598 |  | 0 | 1
1099 | 1098 | Active alarm 599 |  | 0 | 1
1100 | 1099 | Active alarm 600 |  | 0 | 1
1101 | 1100 | Active alarm 601 | Alarm 41:1 MIRU Control no. 4 communication error | 0 | 1
1102 | 1101 | Active alarm 602 | Alarm 41:2 MIRU Control no. 4 motor controller alarm tripped | 0 | 1
1103 | 1102 | Active alarm 603 | Alarm 41:3 MIRU Control no. 4 motor controller communication error | 0 | 1
1104 | 1103 | Active alarm 604 | Alarm 41:4 MIRU Control no. 4 air flow pressure sensor no. 0 communication error | 0 | 1
1105 | 1104 | Active alarm 605 | Alarm 41:5 MIRU Control no. 4 pressure regulation sensor no. 1 communication error | 0 | 1
1106 | 1105 | Active alarm 606 | Alarm 41:6 MIRU Control no. 4 temperature sensor defective | 0 | 1
1107 | 1106 | Active alarm 607 | Alarm 41:7 MIRU Control no. 4 air flow/pressure set point deviation from alarm limit | 0 | 1
1108 | 1107 | Active alarm 608 |  | 0 | 1
1109 | 1108 | Active alarm 609 |  | 0 | 1
1110 | 1109 | Active alarm 610 |  | 0 | 1
1111 | 1110 | Active alarm 611 |  | 0 | 1
1112 | 1111 | Active alarm 612 |  | 0 | 1
1113 | 1112 | Active alarm 613 |  | 0 | 1
1114 | 1113 | Active alarm 614 |  | 0 | 1
1115 | 1114 | Active alarm 615 |  | 0 | 1
1116 | 1115 | Active alarm 616 | Alarm 42:1 MIRU Control no. 5 communication error | 0 | 1
1117 | 1116 | Active alarm 617 | Alarm 42:2 MIRU Control no. 5 motor controller alarm tripped | 0 | 1
1118 | 1117 | Active alarm 618 | Alarm 42:3 MIRU Control no. 5 motor controller communication error | 0 | 1
1119 | 1118 | Active alarm 619 | Alarm 42:4 MIRU Control no. 5 air flow pressure sensor no. 0 communication error | 0 | 1
1120 | 1119 | Active alarm 620 | Alarm 42:5 MIRU Control no. 5 pressure regulation sensor no. 1 communication error | 0 | 1
1121 | 1120 | Active alarm 621 | Alarm 42:6 MIRU Control no. 5 temperature sensor defective | 0 | 1
1122 | 1121 | Active alarm 622 | Alarm 42:7 MIRU Control no. 5 air flow/pressure set point deviation from alarm limit | 0 | 1
1123 | 1122 | Active alarm 623 |  | 0 | 1
1124 | 1123 | Active alarm 624 |  | 0 | 1
1125 | 1124 | Active alarm 625 |  | 0 | 1
1126 | 1125 | Active alarm 626 |  | 0 | 1
1127 | 1126 | Active alarm 627 |  | 0 | 1
1128 | 1127 | Active alarm 628 |  | 0 | 1
1129 | 1128 | Active alarm 629 |  | 0 | 1
1130 | 1129 | Active alarm 630 |  | 0 | 1
1131 | 1130 | Active alarm 631 | Alarm 43:1 MIRU Control no. 6 communication error | 0 | 1
1132 | 1131 | Active alarm 632 | Alarm 43:2 MIRU Control no. 6 motor controller alarm tripped | 0 | 1
1133 | 1132 | Active alarm 633 | Alarm 43:3 MIRU Control no. 6 motor controller communication error | 0 | 1
1134 | 1133 | Active alarm 634 | Alarm 43:4 MIRU Control no. 6 air flow pressure sensor no. 0 communication error | 0 | 1
1135 | 1134 | Active alarm 635 | Alarm 43:5 MIRU Control no. 6 pressure regulation sensor no. 1 communication error | 0 | 1
1136 | 1135 | Active alarm 636 | Alarm 43:6 MIRU Control no. 6 temperature sensor defective | 0 | 1
1137 | 1136 | Active alarm 637 | Alarm 43:7 MIRU Control no. 6 air flow/pressure set point deviation from alarm limit | 0 | 1
1138 | 1137 | Active alarm 638 |  | 0 | 1
1139 | 1138 | Active alarm 639 |  | 0 | 1
1140 | 1139 | Active alarm 640 |  | 0 | 1
1141 | 1140 | Active alarm 641 |  | 0 | 1
1142 | 1141 | Active alarm 642 |  | 0 | 1
1143 | 1142 | Active alarm 643 |  | 0 | 1
1144 | 1143 | Active alarm 644 |  | 0 | 1
1145 | 1144 | Active alarm 645 |  | 0 | 1
1146 | 1145 | Active alarm 646 | Alarm 44:1 MIRU Control no. 7 communication error | 0 | 1
1147 | 1146 | Active alarm 647 | Alarm 44:2 MIRU Control no. 7 motor controller alarm tripped | 0 | 1
1148 | 1147 | Active alarm 648 | Alarm 44:3 MIRU Control no. 7 motor controller communication error | 0 | 1
1149 | 1148 | Active alarm 649 | Alarm 44:4 MIRU Control no. 7 air flow pressure sensor no. 0 communication error | 0 | 1
1150 | 1149 | Active alarm 650 | Alarm 44:5 MIRU Control no. 7 pressure regulation sensor no. 1 communication error | 0 | 1
1151 | 1150 | Active alarm 651 | Alarm 44:6 MIRU Control no. 7 temperature sensor defective | 0 | 1
1152 | 1151 | Active alarm 652 | Alarm 44:7 MIRU Control no. 7 air flow/pressure set point deviation from alarm limit | 0 | 1
1153 | 1152 | Active alarm 653 |  | 0 | 1
1154 | 1153 | Active alarm 654 |  | 0 | 1
1155 | 1154 | Active alarm 655 |  | 0 | 1
1156 | 1155 | Active alarm 656 |  | 0 | 1
1157 | 1156 | Active alarm 657 |  | 0 | 1
1158 | 1157 | Active alarm 658 |  | 0 | 1
1159 | 1158 | Active alarm 659 |  | 0 | 1
1160 | 1159 | Active alarm 660 |  | 0 | 1
1161 | 1160 | Active alarm 661 | Alarm 45:1 MIRU Control no. 8 communication error | 0 | 1
1162 | 1161 | Active alarm 662 | Alarm 45:2 MIRU Control no. 8 motor controller alarm tripped | 0 | 1
1163 | 1162 | Active alarm 663 | Alarm 45:3 MIRU Control no. 8 motor controller communication error | 0 | 1
1164 | 1163 | Active alarm 664 | Alarm 45:4 MIRU Control no. 8 air flow pressure sensor no. 0 communication error | 0 | 1
1165 | 1164 | Active alarm 665 | Alarm 45:5 MIRU Control no. 8 pressure regulation sensor no. 1 communication error | 0 | 1
1166 | 1165 | Active alarm 666 | Alarm 45:6 MIRU Control no. 8 temperature sensor defective | 0 | 1
1167 | 1166 | Active alarm 667 | Alarm 45:7 MIRU Control no. 8 air flow/pressure set point deviation from alarm limit | 0 | 1
1168 | 1167 | Active alarm 668 |  | 0 | 1
1169 | 1168 | Active alarm 669 |  | 0 | 1
1170 | 1169 | Active alarm 670 |  | 0 | 1
1171 | 1170 | Active alarm 671 |  | 0 | 1
1172 | 1171 | Active alarm 672 |  | 0 | 1
1173 | 1172 | Active alarm 673 |  | 0 | 1
1174 | 1173 | Active alarm 674 |  | 0 | 1
1175 | 1174 | Active alarm 675 |  | 0 | 1
1176 | 1175 | Active alarm 676 | Alarm 46:1 MIRU Control no. 9 communication error | 0 | 1
1177 | 1176 | Active alarm 677 | Alarm 46:2 MIRU Control no. 9 motor controller alarm tripped | 0 | 1
1178 | 1177 | Active alarm 678 | Alarm 46:3 MIRU Control no. 9 motor controller communication error | 0 | 1
1179 | 1178 | Active alarm 679 | Alarm 46:4 MIRU Control no. 9 air flow pressure sensor no. 0 communication error | 0 | 1
1180 | 1179 | Active alarm 680 | Alarm 46:5 MIRU Control no. 9 pressure regulation sensor no. 1 communication error | 0 | 1
1181 | 1180 | Active alarm 681 | Alarm 46:6 MIRU Control no. 9 temperature sensor defective | 0 | 1
1182 | 1181 | Active alarm 682 | Alarm 46:7 MIRU Control no. 9 air flow/pressure set point deviation from alarm limit | 0 | 1
1183 | 1182 | Active alarm 683 |  | 0 | 1
1184 | 1183 | Active alarm 684 |  | 0 | 1
1185 | 1184 | Active alarm 685 |  | 0 | 1
1186 | 1185 | Active alarm 686 |  | 0 | 1
1187 | 1186 | Active alarm 687 |  | 0 | 1
1188 | 1187 | Active alarm 688 |  | 0 | 1
1189 | 1188 | Active alarm 689 |  | 0 | 1
1190 | 1189 | Active alarm 690 |  | 0 | 1
1191 | 1190 | Active alarm 691 | Alarm 47:1 MIRU Control no. 10 communication error | 0 | 1
1192 | 1191 | Active alarm 692 | Alarm 47:2 MIRU Control no. 10 motor controller alarm tripped | 0 | 1
1193 | 1192 | Active alarm 693 | Alarm 47:3 MIRU Control no. 10 motor controller communication error | 0 | 1
1194 | 1193 | Active alarm 694 | Alarm 47:4 MIRU Control no. 10 air flow pressure sensor no. 0 communication error | 0 | 1
1195 | 1194 | Active alarm 695 | Alarm 47:5 MIRU Control no. 10 pressure regulation sensor no. 1 communication error | 0 | 1
1196 | 1195 | Active alarm 696 | Alarm 47:6 MIRU Control no. 10 temperature sensor defective | 0 | 1
1197 | 1196 | Active alarm 697 | Alarm 47:7 MIRU Control no. 10 air flow/pressure set point deviation from alarm limit | 0 | 1
1198 | 1197 | Active alarm 698 |  | 0 | 1
1199 | 1198 | Active alarm 699 |  | 0 | 1
1200 | 1199 | Active alarm 700 |  | 0 | 1
1201 | 1200 | Active alarm 701 |  | 0 | 1
1202 | 1201 | Active alarm 702 |  | 0 | 1
1203 | 1202 | Active alarm 703 |  | 0 | 1
1204 | 1203 | Active alarm 704 |  | 0 | 1
1205 | 1204 | Active alarm 705 |  | 0 | 1
1206 | 1205 | Active alarm 706 |  | 0 | 1
1207 | 1206 | Active alarm 707 |  | 0 | 1
1208 | 1207 | Active alarm 708 |  | 0 | 1
1209 | 1208 | Active alarm 709 |  | 0 | 1
1210 | 1209 | Active alarm 710 |  | 0 | 1
1211 | 1210 | Active alarm 711 |  | 0 | 1
1212 | 1211 | Active alarm 712 |  | 0 | 1
1213 | 1212 | Active alarm 713 |  | 0 | 1
1214 | 1213 | Active alarm 714 |  | 0 | 1
1215 | 1214 | Active alarm 715 |  | 0 | 1
1216 | 1215 | Active alarm 716 |  | 0 | 1
1217 | 1216 | Active alarm 717 |  | 0 | 1
1218 | 1217 | Active alarm 718 |  | 0 | 1
1219 | 1218 | Active alarm 719 |  | 0 | 1
1220 | 1219 | Active alarm 720 |  | 0 | 1
1221 | 1220 | Active alarm 721 | Alarm 49:1 Supply air fan no. 1A communication error | 0 | 1
1222 | 1221 | Active alarm 722 | Alarm 49:2 Supply air fan no. 1A motor controller over current | 0 | 1
1223 | 1222 | Active alarm 723 | Alarm 49:3 Supply air fan no. 1A motor controller under voltage | 0 | 1
1224 | 1223 | Active alarm 724 | Alarm 49:4 Supply air fan no. 1A motor controller over voltage | 0 | 1
1225 | 1224 | Active alarm 725 | Alarm 49:5 Supply air fan no. 1A motor controller over temperature | 0 | 1
1226 | 1225 | Active alarm 726 | Alarm 49:6 Supply air fan no. 1A motor controller start error | 0 | 1
1227 | 1226 | Active alarm 727 | Alarm 49:7 Supply air fan no. 1A motor controller ripple error | 0 | 1
1228 | 1227 | Active alarm 728 | Alarm 49:8 Supply air fan no. 1A motor controller phase error | 0 | 1
1229 | 1228 | Active alarm 729 | Alarm 49:9 Supply air fan no. 1A motor controller internal memory error | 0 | 1
1230 | 1229 | Active alarm 730 | Alarm 49:10 Supply air fan no. 1A motor controller current reduction | 0 | 1
1231 | 1230 | Active alarm 731 | Alarm 49:11 Supply air fan no. 1A motor controller internal com. error | 0 | 1 |  |  | 1.18
1232 | 1231 | Active alarm 732 |  | 0 | 1
1233 | 1232 | Active alarm 733 |  | 0 | 1
1234 | 1233 | Active alarm 734 |  | 0 | 1
1235 | 1234 | Active alarm 735 |  | 0 | 1
1236 | 1235 | Active alarm 736 | Alarm 50:1 Supply air fan no. 2A communication error | 0 | 1
1237 | 1236 | Active alarm 737 | Alarm 50:2 Supply air fan no. 2A motor controller over current | 0 | 1
1238 | 1237 | Active alarm 738 | Alarm 50:3 Supply air fan no. 2A motor controller under voltage | 0 | 1
1239 | 1238 | Active alarm 739 | Alarm 50:4 Supply air fan no. 2A motor controller over voltage | 0 | 1
1240 | 1239 | Active alarm 740 | Alarm 50:5 Supply air fan no. 2A motor controller over temperature | 0 | 1
1241 | 1240 | Active alarm 741 | Alarm 50:6 Supply air fan no. 2A motor controller start error | 0 | 1
1242 | 1241 | Active alarm 742 | Alarm 50:7 Supply air fan no. 2A motor controller ripple error | 0 | 1
1243 | 1242 | Active alarm 743 | Alarm 50:8 Supply air fan no. 2A motor controller phase error | 0 | 1
1244 | 1243 | Active alarm 744 | Alarm 50:9 Supply air fan no. 2A motor controller internal memory error | 0 | 1
1245 | 1244 | Active alarm 745 | Alarm 50:10 Supply air fan no. 2A motor controller current reduction | 0 | 1
1246 | 1245 | Active alarm 746 | Alarm 50:11 Supply air fan no. 2A motor controller internal com. Error | 0 | 1 |  |  | 1.18
1247 | 1246 | Active alarm 747 |  | 0 | 1
1248 | 1247 | Active alarm 748 |  | 0 | 1
1249 | 1248 | Active alarm 749 |  | 0 | 1
1250 | 1249 | Active alarm 750 |  | 0 | 1
1251 | 1250 | Active alarm 751 | Alarm 51:1 Supply air fan no. 3A communication error | 0 | 1
1252 | 1251 | Active alarm 752 | Alarm 51:2 Supply air fan no. 3A motor controller over current | 0 | 1
1253 | 1252 | Active alarm 753 | Alarm 51:3 Supply air fan no. 3A motor controller under voltage | 0 | 1
1254 | 1253 | Active alarm 754 | Alarm 51:4 Supply air fan no. 3A motor controller over voltage | 0 | 1
1255 | 1254 | Active alarm 755 | Alarm 51:5 Supply air fan no. 3A motor controller over temperature | 0 | 1
1256 | 1255 | Active alarm 756 | Alarm 51:6 Supply air fan no. 3A motor controller start error | 0 | 1
1257 | 1256 | Active alarm 757 | Alarm 51:7 Supply air fan no. 3A motor controller ripple error | 0 | 1
1258 | 1257 | Active alarm 758 | Alarm 51:8 Supply air fan no. 3A motor controller phase error | 0 | 1
1259 | 1258 | Active alarm 759 | Alarm 51:9 Supply air fan no. 3A motor controller internal memory error | 0 | 1
1260 | 1259 | Active alarm 760 | Alarm 51:10 Supply air fan no. 3A motor controller current reduction | 0 | 1
1261 | 1260 | Active alarm 761 | Alarm 51:11 Supply air fan no. 3A motor controller internal com. error | 0 | 1 |  |  | 1.18
1262 | 1261 | Active alarm 762 |  | 0 | 1
1263 | 1262 | Active alarm 763 |  | 0 | 1
1264 | 1263 | Active alarm 764 |  | 0 | 1
1265 | 1264 | Active alarm 765 |  | 0 | 1
1266 | 1265 | Active alarm 766 | Alarm 52:1 Supply air fan no. 1B communication error | 0 | 1
1267 | 1266 | Active alarm 767 | Alarm 52:2 Supply air fan no. 1B motor controller over current | 0 | 1
1268 | 1267 | Active alarm 768 | Alarm 52:3 Supply air fan no. 1B motor controller under voltage | 0 | 1
1269 | 1268 | Active alarm 769 | Alarm 52:4 Supply air fan no. 1B motor controller over voltage | 0 | 1
1270 | 1269 | Active alarm 770 | Alarm 52:5 Supply air fan no. 1B motor controller over temperature | 0 | 1
1271 | 1270 | Active alarm 771 | Alarm 52:6 Supply air fan no. 1B motor controller start error | 0 | 1
1272 | 1271 | Active alarm 772 | Alarm 52:7 Supply air fan no. 1B motor controller ripple error | 0 | 1
1273 | 1272 | Active alarm 773 | Alarm 52:8 Supply air fan no. 1B motor controller phase error | 0 | 1
1274 | 1273 | Active alarm 774 | Alarm 52:9 Supply air fan no. 1B motor controller internal memory error | 0 | 1
1275 | 1274 | Active alarm 775 | Alarm 52:10 Supply air fan no. 1B motor controller current reduction | 0 | 1
1276 | 1275 | Active alarm 776 |  | 0 | 1
1277 | 1276 | Active alarm 777 |  | 0 | 1
1278 | 1277 | Active alarm 778 |  | 0 | 1
1279 | 1278 | Active alarm 779 |  | 0 | 1
1280 | 1279 | Active alarm 780 |  | 0 | 1
1281 | 1280 | Active alarm 781 | Alarm 53:1 Supply air fan no. 2B communication error | 0 | 1
1282 | 1281 | Active alarm 782 | Alarm 53:2 Supply air fan no. 2B motor controller over current | 0 | 1
1283 | 1282 | Active alarm 783 | Alarm 53:3 Supply air fan no. 2B motor controller under voltage | 0 | 1
1284 | 1283 | Active alarm 784 | Alarm 53:4 Supply air fan no. 2B motor controller over voltage | 0 | 1
1285 | 1284 | Active alarm 785 | Alarm 53:5 Supply air fan no. 2B motor controller over temperature | 0 | 1
1286 | 1285 | Active alarm 786 | Alarm 53:6 Supply air fan no. 2B motor controller start error | 0 | 1
1287 | 1286 | Active alarm 787 | Alarm 53:7 Supply air fan no. 2B motor controller ripple error | 0 | 1
1288 | 1287 | Active alarm 788 | Alarm 53:8 Supply air fan no. 2B motor controller phase error | 0 | 1
1289 | 1288 | Active alarm 789 | Alarm 53:9 Supply air fan no. 2B motor controller internal memory error | 0 | 1
1290 | 1289 | Active alarm 790 | Alarm 53:10 Supply air fan no. 2B motor controller current reduction | 0 | 1
1291 | 1290 | Active alarm 791 |  | 0 | 1
1292 | 1291 | Active alarm 792 |  | 0 | 1
1293 | 1292 | Active alarm 793 |  | 0 | 1
1294 | 1293 | Active alarm 794 |  | 0 | 1
1295 | 1294 | Active alarm 795 |  | 0 | 1
1296 | 1295 | Active alarm 796 | Alarm 54:1 Supply air fan no. 3B communication error | 0 | 1
1297 | 1296 | Active alarm 797 | Alarm 54:2 Supply air fan no. 3B motor controller over current | 0 | 1
1298 | 1297 | Active alarm 798 | Alarm 54:3 Supply air fan no. 3B motor controller under voltage | 0 | 1
1299 | 1298 | Active alarm 799 | Alarm 54:4 Supply air fan no. 3B motor controller over voltage | 0 | 1
1300 | 1299 | Active alarm 800 | Alarm 54:5 Supply air fan no. 3B motor controller over temperature | 0 | 1
1301 | 1300 | Active alarm 801 | Alarm 54:6 Supply air fan no. 3B motor controller start error | 0 | 1
1302 | 1301 | Active alarm 802 | Alarm 54:7 Supply air fan no. 3B motor controller ripple error | 0 | 1
1303 | 1302 | Active alarm 803 | Alarm 54:8 Supply air fan no. 3B motor controller phase error | 0 | 1
1304 | 1303 | Active alarm 804 | Alarm 54:9 Supply air fan no. 3B motor controller internal memory error | 0 | 1
1305 | 1304 | Active alarm 805 | Alarm 54:10 Supply air fan no. 3B motor controller current reduction | 0 | 1
1306 | 1305 | Active alarm 806 |  | 0 | 1
1307 | 1306 | Active alarm 807 |  | 0 | 1
1308 | 1307 | Active alarm 808 |  | 0 | 1
1309 | 1308 | Active alarm 809 |  | 0 | 1
1310 | 1309 | Active alarm 810 |  | 0 | 1
1311 | 1310 | Active alarm 811 | Alarm 55:1 Extract air fan no. 1A communication error | 0 | 1
1312 | 1311 | Active alarm 812 | Alarm 55:2 Extract air fan no. 1A motor controller over current | 0 | 1
1313 | 1312 | Active alarm 813 | Alarm 55:3 Extract air fan no. 1A motor controller under voltage | 0 | 1
1314 | 1313 | Active alarm 814 | Alarm 55:4 Extract air fan no. 1A motor controller over voltage | 0 | 1
1315 | 1314 | Active alarm 815 | Alarm 55:5 Extract air fan no. 1A motor controller over temperature | 0 | 1
1316 | 1315 | Active alarm 816 | Alarm 55:6 Extract air fan no. 1A motor controller start error | 0 | 1
1317 | 1316 | Active alarm 817 | Alarm 55:7 Extract air fan no. 1A motor controller ripple error | 0 | 1
1318 | 1317 | Active alarm 818 | Alarm 55:8 Extract air fan no. 1A motor controller phase error | 0 | 1
1319 | 1318 | Active alarm 819 | Alarm 55:9 Extract air fan no. 1A motor controller internal memory error | 0 | 1
1320 | 1319 | Active alarm 820 | Alarm 55:10 Extract air fan no. 1A motor controller current reduction | 0 | 1
1321 | 1320 | Active alarm 821 | Alarm 55:11 Extract air fan no. 1A motor controller internal com. error | 0 | 1 |  |  | 1.18
1322 | 1321 | Active alarm 822 |  | 0 | 1
1323 | 1322 | Active alarm 823 |  | 0 | 1
1324 | 1323 | Active alarm 824 |  | 0 | 1
1325 | 1324 | Active alarm 825 |  | 0 | 1
1326 | 1325 | Active alarm 826 | Alarm 56:1 Extract air fan no. 2A communication error | 0 | 1
1327 | 1326 | Active alarm 827 | Alarm 56:2 Extract air fan no. 2A motor controller over current | 0 | 1
1328 | 1327 | Active alarm 828 | Alarm 56:3 Extract air fan no. 2A motor controller under voltage | 0 | 1
1329 | 1328 | Active alarm 829 | Alarm 56:4 Extract air fan no. 2A motor controller over voltage | 0 | 1
1330 | 1329 | Active alarm 830 | Alarm 56:5 Extract air fan no. 2A motor controller over temperature | 0 | 1
1331 | 1330 | Active alarm 831 | Alarm 56:6 Extract air fan no. 2A motor controller start error | 0 | 1
1332 | 1331 | Active alarm 832 | Alarm 56:7 Extract air fan no. 2A motor controller ripple error | 0 | 1
1333 | 1332 | Active alarm 833 | Alarm 56:8 Extract air fan no. 2A motor controller phase error | 0 | 1
1334 | 1333 | Active alarm 834 | Alarm 56:9 Extract air fan no. 2A motor controller internal memory error | 0 | 1
1335 | 1334 | Active alarm 835 | Alarm 56:10 Extract air fan no. 2A motor controller current reduction | 0 | 1
1336 | 1335 | Active alarm 836 | Alarm 56:11 Extract air fan no. 2A motor controller internal com. Error | 0 | 1 |  |  | 1.18
1337 | 1336 | Active alarm 837 |  | 0 | 1
1338 | 1337 | Active alarm 838 |  | 0 | 1
1339 | 1338 | Active alarm 839 |  | 0 | 1
1340 | 1339 | Active alarm 840 |  | 0 | 1
1341 | 1340 | Active alarm 841 | Alarm 57:1 Extract air fan no. 3A communication error | 0 | 1
1342 | 1341 | Active alarm 842 | Alarm 57:2 Extract air fan no. 3A motor controller over current | 0 | 1
1343 | 1342 | Active alarm 843 | Alarm 57:3 Extract air fan no. 3A motor controller under voltage | 0 | 1
1344 | 1343 | Active alarm 844 | Alarm 57:4 Extract air fan no. 3A motor controller over voltage | 0 | 1
1345 | 1344 | Active alarm 845 | Alarm 57:5 Extract air fan no. 3A motor controller over temperature | 0 | 1
1346 | 1345 | Active alarm 846 | Alarm 57:6 Extract air fan no. 3A motor controller start error | 0 | 1
1347 | 1346 | Active alarm 847 | Alarm 57:7 Extract air fan no. 3A motor controller ripple error | 0 | 1
1348 | 1347 | Active alarm 848 | Alarm 57:8 Extract air fan no. 3A motor controller phase error | 0 | 1
1349 | 1348 | Active alarm 849 | Alarm 57:9 Extract air fan no. 3A motor controller internal memory error | 0 | 1
1350 | 1349 | Active alarm 850 | Alarm 57:10 Extract air fan no. 3A motor controller current reduction | 0 | 1
1351 | 1350 | Active alarm 851 | Alarm 57:11 Extract air fan no. 3A motor controller internal com. error | 0 | 1 |  |  | 1.18
1352 | 1351 | Active alarm 852 |  | 0 | 1
1353 | 1352 | Active alarm 853 |  | 0 | 1
1354 | 1353 | Active alarm 854 |  | 0 | 1
1355 | 1354 | Active alarm 855 |  | 0 | 1
1356 | 1355 | Active alarm 856 | Alarm 58:1 Extract air fan no. 1B communication error | 0 | 1
1357 | 1356 | Active alarm 857 | Alarm 58:2 Extract air fan no. 1B motor controller over current | 0 | 1
1358 | 1357 | Active alarm 858 | Alarm 58:3 Extract air fan no. 1B motor controller under voltage | 0 | 1
1359 | 1358 | Active alarm 859 | Alarm 58:4 Extract air fan no. 1B motor controller over voltage | 0 | 1
1360 | 1359 | Active alarm 860 | Alarm 58:5 Extract air fan no. 1B motor controller over temperature | 0 | 1
1361 | 1360 | Active alarm 861 | Alarm 58:6 Extract air fan no. 1B motor controller start error | 0 | 1
1362 | 1361 | Active alarm 862 | Alarm 58:7 Extract air fan no. 1B motor controller ripple error | 0 | 1
1363 | 1362 | Active alarm 863 | Alarm 58:8 Extract air fan no. 1B motor controller phase error | 0 | 1
1364 | 1363 | Active alarm 864 | Alarm 58:9 Extract air fan no. 1B motor controller internal memory error | 0 | 1
1365 | 1364 | Active alarm 865 | Alarm 58:10 Extract air fan no. 1B motor controller current reduction | 0 | 1
1366 | 1365 | Active alarm 866 |  | 0 | 1
1367 | 1366 | Active alarm 867 |  | 0 | 1
1368 | 1367 | Active alarm 868 |  | 0 | 1
1369 | 1368 | Active alarm 869 |  | 0 | 1
1370 | 1369 | Active alarm 870 |  | 0 | 1
1371 | 1370 | Active alarm 871 | Alarm 59:1 Extract air fan no. 2B communication error | 0 | 1
1372 | 1371 | Active alarm 872 | Alarm 59:2 Extract air fan no. 2B motor controller over current | 0 | 1
1373 | 1372 | Active alarm 873 | Alarm 59:3 Extract air fan no. 2B motor controller under voltage | 0 | 1
1374 | 1373 | Active alarm 874 | Alarm 59:4 Extract air fan no. 2B motor controller over voltage | 0 | 1
1375 | 1374 | Active alarm 875 | Alarm 59:5 Extract air fan no. 2B motor controller over temperature | 0 | 1
1376 | 1375 | Active alarm 876 | Alarm 59:6 Extract air fan no. 2B motor controller start error | 0 | 1
1377 | 1376 | Active alarm 877 | Alarm 59:7 Extract air fan no. 2B motor controller ripple error | 0 | 1
1378 | 1377 | Active alarm 878 | Alarm 59:8 Extract air fan no. 2B motor controller phase error | 0 | 1
1379 | 1378 | Active alarm 879 | Alarm 59:9 Extract air fan no. 2B motor controller internal memory error | 0 | 1
1380 | 1379 | Active alarm 880 | Alarm 59:10 Extract air fan no. 2B motor controller current reduction | 0 | 1
1381 | 1380 | Active alarm 881 |  | 0 | 1
1382 | 1381 | Active alarm 882 |  | 0 | 1
1383 | 1382 | Active alarm 883 |  | 0 | 1
1384 | 1383 | Active alarm 884 |  | 0 | 1
1385 | 1384 | Active alarm 885 |  | 0 | 1
1386 | 1385 | Active alarm 886 | Alarm 60:1 Extract air fan no. 3B communication error | 0 | 1
1387 | 1386 | Active alarm 887 | Alarm 60:2 Extract air fan no. 3B motor controller over current | 0 | 1
1388 | 1387 | Active alarm 888 | Alarm 60:3 Extract air fan no. 3B motor controller under voltage | 0 | 1
1389 | 1388 | Active alarm 889 | Alarm 60:4 Extract air fan no. 3B motor controller over voltage | 0 | 1
1390 | 1389 | Active alarm 890 | Alarm 60:5 Extract air fan no. 3B motor controller over temperature | 0 | 1
1391 | 1390 | Active alarm 891 | Alarm 60:6 Extract air fan no. 3B motor controller start error | 0 | 1
1392 | 1391 | Active alarm 892 | Alarm 60:7 Extract air fan no. 3B motor controller ripple error | 0 | 1
1393 | 1392 | Active alarm 893 | Alarm 60:8 Extract air fan no. 3B motor controller phase error | 0 | 1
1394 | 1393 | Active alarm 894 | Alarm 60:9 Extract air fan no. 3B motor controller internal memory error | 0 | 1
1395 | 1394 | Active alarm 895 | Alarm 60:10 Extract air fan no. 3B motor controller current reduction | 0 | 1
1396 | 1395 | Active alarm 896 |  | 0 | 1
1397 | 1396 | Active alarm 897 |  | 0 | 1
1398 | 1397 | Active alarm 898 |  | 0 | 1
1399 | 1398 | Active alarm 899 |  | 0 | 1
1400 | 1399 | Active alarm 900 |  | 0 | 1
1401 | 1400 | Active alarm 901 | Alarm 61:1 Supply air fan no. 1A I/O-module com. error | 0 | 1 |  |  | 1.18
1402 | 1401 | Active alarm 902 |  | 0 | 1
1403 | 1402 | Active alarm 903 |  | 0 | 1
1404 | 1403 | Active alarm 904 |  | 0 | 1
1405 | 1404 | Active alarm 905 |  | 0 | 1
1406 | 1405 | Active alarm 906 | Alarm 61:6 Supply air fan no. 2A I/O-module com. error | 0 | 1 |  |  | 1.18
1407 | 1406 | Active alarm 907 |  | 0 | 1
1408 | 1407 | Active alarm 908 |  | 0 | 1
1409 | 1408 | Active alarm 909 |  | 0 | 1
1410 | 1409 | Active alarm 910 |  | 0 | 1
1411 | 1410 | Active alarm 911 | Alarm 61:11 Supply air fan no. 3A I/O-module com. error | 0 | 1 |  |  | 1.18
1412 | 1411 | Active alarm 912 |  | 0 | 1
1413 | 1412 | Active alarm 913 |  | 0 | 1
1414 | 1413 | Active alarm 914 |  | 0 | 1
1415 | 1414 | Active alarm 915 |  | 0 | 1
1416 | 1415 | Active alarm 916 | Alarm 62:1 Extract air fan no. 1A I/O-module com. error | 0 | 1 |  |  | 1.18
1417 | 1416 | Active alarm 917 |  | 0 | 1
1418 | 1417 | Active alarm 918 |  | 0 | 1
1419 | 1418 | Active alarm 919 |  | 0 | 1
1420 | 1419 | Active alarm 920 |  | 0 | 1
1421 | 1420 | Active alarm 921 | Alarm 62:6 Extract air fan no. 2A I/O-module com. error | 0 | 1 |  |  | 1.18
1422 | 1421 | Active alarm 922 |  | 0 | 1
1423 | 1422 | Active alarm 923 |  | 0 | 1
1424 | 1423 | Active alarm 924 |  | 0 | 1
1425 | 1424 | Active alarm 925 |  | 0 | 1
1426 | 1425 | Active alarm 926 | Alarm 62:11 Extract air fan no. 3A I/O-module com. error | 0 | 1 |  |  | 1.18
1427 | 1426 | Active alarm 927 |  | 0 | 1
1428 | 1427 | Active alarm 928 |  | 0 | 1
1429 | 1428 | Active alarm 929 |  | 0 | 1
1430 | 1429 | Active alarm 930 |  | 0 | 1
1431 | 1430 | Active alarm 931 | Alarm 63:1 MIRU 1 I/O-module com. error | 0 | 1 |  |  | 1.25
1432 | 1431 | Active alarm 932 |  | 0 | 1
1433 | 1432 | Active alarm 933 |  | 0 | 1
1434 | 1433 | Active alarm 934 |  | 0 | 1
1435 | 1434 | Active alarm 935 |  | 0 | 1
1436 | 1435 | Active alarm 936 | Alarm 63:6 MIRU 2 I/O-module com. error | 0 | 1 |  |  | 1.25
1437 | 1436 | Active alarm 937 |  | 0 | 1
1438 | 1437 | Active alarm 938 |  | 0 | 1
1439 | 1438 | Active alarm 939 |  | 0 | 1
1440 | 1439 | Active alarm 940 |  | 0 | 1
1441 | 1440 | Active alarm 941 | Alarm 63:11 MIRU 3 I/O-module com. error | 0 | 1 |  |  | 1.25
1442 | 1441 | Active alarm 942 |  | 0 | 1
1443 | 1442 | Active alarm 943 |  | 0 | 1
1444 | 1443 | Active alarm 944 |  | 0 | 1
1445 | 1444 | Active alarm 945 |  | 0 | 1
1446 | 1445 | Active alarm 946 | Alarm 64:1 Supply air fan no. 1A common A-alarm | 0 | 1 |  |  | 2.38
1447 | 1446 | Active alarm 947 |  | 0 | 1
1448 | 1447 | Active alarm 948 | Alarm 64:3 Supply air fan no. 1A common B-alarm | 0 | 1 |  |  | 2.38
1449 | 1448 | Active alarm 949 |  | 0 | 1
1450 | 1449 | Active alarm 950 | Alarm 64:5 Supply air fan no. 1A common warning | 0 | 1 |  |  | 2.38
1451 | 1450 | Active alarm 951 | Alarm 64:6 Supply air fan no. 2A common A-alarm | 0 | 1 |  |  | 2.38
1452 | 1451 | Active alarm 952 |  | 0 | 1
1453 | 1452 | Active alarm 953 | Alarm 64:8 Supply air fan no. 2A common B-alarm | 0 | 1 |  |  | 2.38
1454 | 1453 | Active alarm 954 |  | 0 | 1
1455 | 1454 | Active alarm 955 | Alarm 64:10 Supply air fan no. 2A common warning | 0 | 1 |  |  | 2.38
1456 | 1455 | Active alarm 956 | Alarm 64:11 Supply air fan no. 3A common A-alarm | 0 | 1 |  |  | 2.38
1457 | 1456 | Active alarm 957 |  | 0 | 1
1458 | 1457 | Active alarm 958 | Alarm 64:13 Supply air fan no. 3A common B-alarm | 0 | 1 |  |  | 2.38
1459 | 1458 | Active alarm 959 |  | 0 | 1
1460 | 1459 | Active alarm 960 | Alarm 64:15 Supply air fan no. 3A common warning | 0 | 1 |  |  | 2.38
1461 | 1460 | Active alarm 961 | Alarm 65:1 Extract air fan no. 1A common A-alarm | 0 | 1 |  |  | 2.38
1462 | 1461 | Active alarm 962 |  | 0 | 1
1463 | 1462 | Active alarm 963 | Alarm 65:3 Extract air fan no. 1A common B-alarm | 0 | 1 |  |  | 2.38
1464 | 1463 | Active alarm 964 |  | 0 | 1
1465 | 1464 | Active alarm 965 | Alarm 65:5 Extract air fan no. 1A common warning | 0 | 1 |  |  | 2.38
1466 | 1465 | Active alarm 966 | Alarm 65:6 Extract air fan no. 2A common A-alarm | 0 | 1 |  |  | 2.38
1467 | 1466 | Active alarm 967 |  | 0 | 1
1468 | 1467 | Active alarm 968 | Alarm 65:8 Extract air fan no. 2A common B-alarm | 0 | 1 |  |  | 2.38
1469 | 1468 | Active alarm 969 |  | 0 | 1
1470 | 1469 | Active alarm 970 | Alarm 65:10 Extract air fan no. 2A common warning | 0 | 1 |  |  | 2.38
1471 | 1470 | Active alarm 971 | Alarm 65:11 Extract air fan no. 3A common A-alarm | 0 | 1 |  |  | 2.38
1472 | 1471 | Active alarm 972 |  | 0 | 1
1473 | 1472 | Active alarm 973 | Alarm 65:13 Extract air fan no. 3A common B-alarm | 0 | 1 |  |  | 2.38
1474 | 1473 | Active alarm 974 |  | 0 | 1
1475 | 1474 | Active alarm 975 | Alarm 65:15 Extract air fan no. 3A common warning | 0 | 1 |  |  | 2.38
1476 | 1475 | Active alarm 976 |  | 0 | 1
1477 | 1476 | Active alarm 977 |  | 0 | 1
1478 | 1477 | Active alarm 978 |  | 0 | 1
1479 | 1478 | Active alarm 979 |  | 0 | 1
1480 | 1479 | Active alarm 980 |  | 0 | 1
1481 | 1480 | Active alarm 981 |  | 0 | 1
1482 | 1481 | Active alarm 982 |  | 0 | 1
1483 | 1482 | Active alarm 983 |  | 0 | 1
1484 | 1483 | Active alarm 984 |  | 0 | 1
1485 | 1484 | Active alarm 985 |  | 0 | 1
1486 | 1485 | Active alarm 986 |  | 0 | 1
1487 | 1486 | Active alarm 987 |  | 0 | 1
1488 | 1487 | Active alarm 988 |  | 0 | 1
1489 | 1488 | Active alarm 989 |  | 0 | 1
1490 | 1489 | Active alarm 990 |  | 0 | 1
1491 | 1490 | Active alarm 991 |  | 0 | 1
1492 | 1491 | Active alarm 992 |  | 0 | 1
1493 | 1492 | Active alarm 993 |  | 0 | 1
1494 | 1493 | Active alarm 994 |  | 0 | 1
1495 | 1494 | Active alarm 995 |  | 0 | 1
1496 | 1495 | Active alarm 996 |  | 0 | 1
1497 | 1496 | Active alarm 997 |  | 0 | 1
1498 | 1497 | Active alarm 998 |  | 0 | 1
1499 | 1498 | Active alarm 999 |  | 0 | 1
1500 | 1499 | Active alarm 1000 |  | 0 | 1
1501 | 1500 | Active alarm 1001 |  | 0 | 1
1502 | 1501 | Active alarm 1002 |  | 0 | 1
1503 | 1502 | Active alarm 1003 |  | 0 | 1
1504 | 1503 | Active alarm 1004 |  | 0 | 1
1505 | 1504 | Active alarm 1005 |  | 0 | 1
1506 | 1505 | Active alarm 1006 |  | 0 | 1
1507 | 1506 | Active alarm 1007 |  | 0 | 1
1508 | 1507 | Active alarm 1008 |  | 0 | 1
1509 | 1508 | Active alarm 1009 |  | 0 | 1
1510 | 1509 | Active alarm 1010 |  | 0 | 1
1511 | 1510 | Active alarm 1011 |  | 0 | 1
1512 | 1511 | Active alarm 1012 |  | 0 | 1
1513 | 1512 | Active alarm 1013 |  | 0 | 1
1514 | 1513 | Active alarm 1014 |  | 0 | 1
1515 | 1514 | Active alarm 1015 |  | 0 | 1
1516 | 1515 | Active alarm 1016 |  | 0 | 1
1517 | 1516 | Active alarm 1017 |  | 0 | 1
1518 | 1517 | Active alarm 1018 |  | 0 | 1
1519 | 1518 | Active alarm 1019 |  | 0 | 1
1520 | 1519 | Active alarm 1020 |  | 0 | 1
1521 | 1520 | Active alarm 1021 |  | 0 | 1
1522 | 1521 | Active alarm 1022 |  | 0 | 1
1523 | 1522 | Active alarm 1023 |  | 0 | 1
1524 | 1523 | Active alarm 1024 |  | 0 | 1
1525 | 1524 | Active alarm 1025 |  | 0 | 1
1526 | 1525 | Active alarm 1026 |  | 0 | 1
1527 | 1526 | Active alarm 1027 |  | 0 | 1
1528 | 1527 | Active alarm 1028 |  | 0 | 1
1529 | 1528 | Active alarm 1029 |  | 0 | 1
1530 | 1529 | Active alarm 1030 |  | 0 | 1
1531 | 1530 | Active alarm 1031 |  | 0 | 1
1532 | 1531 | Active alarm 1032 |  | 0 | 1
1533 | 1532 | Active alarm 1033 |  | 0 | 1
1534 | 1533 | Active alarm 1034 |  | 0 | 1
1535 | 1534 | Active alarm 1035 |  | 0 | 1
1536 | 1535 | Active alarm 1036 | Alarm 70:1 H/C controls com. Error | 0 | 1 |  |  | 1.23
1537 | 1536 | Active alarm 1037 | Alarm 70:2 H/C controls internal memory error | 0 | 1 |  |  | 1.23
1538 | 1537 | Active alarm 1038 | Alarm 70:3 H/C controls clock circuit defective | 0 | 1 |  |  | 1.23
1539 | 1538 | Active alarm 1039 |  | 0 | 1
1540 | 1539 | Active alarm 1040 | Alarm 70:5 H/C defrost pressure sensor no. D com. Error | 0 | 1 |  |  | 1.23
1541 | 1540 | Active alarm 1041 | Alarm 70:6 H/C defrost I/O-module no. 5 com. Error | 0 | 1 |  |  | 1.23
1542 | 1541 | Active alarm 1042 | Alarm 70:7 H/C defrost recirculation damper monitoring tripped | 0 | 1 |  |  | 1.23
1543 | 1542 | Active alarm 1043 | Alarm 70:8 H/C defrost electrical heater overheat protection tripped | 0 | 1 |  |  | 1.23
1544 | 1543 | Active alarm 1044 | Alarm 70:9 H/C defrost time above alarm limit | 0 | 1 |  |  | 1.23
1545 | 1544 | Active alarm 1045 |  | 0 | 1
1546 | 1545 | Active alarm 1046 | Alarm 70:11 H/C defrost interval above alarm limit | 0 | 1 |  |  | 1.27
1547 | 1546 | Active alarm 1047 | Alarm 70:12 H/C wrong phase sequence | 0 | 1 |  |  | 1.27
1548 | 1547 | Active alarm 1048 |  | 0 | 1
1549 | 1548 | Active alarm 1049 |  | 0 | 1
1550 | 1549 | Active alarm 1050 |  | 0 | 1
1551 | 1550 | Active alarm 1051 | Alarm 71:1 H/C compressor motor control com. Error | 0 | 1 |  |  | 1.23
1552 | 1551 | Active alarm 1052 | Alarm 71:2 H/C compressor motor control start error | 0 | 1 |  |  | 1.23
1553 | 1552 | Active alarm 1053 | Alarm 71:3 H/C compressor motor controller over or under voltage | 0 | 1 |  |  | 1.23
1554 | 1553 | Active alarm 1054 | Alarm 71:4 H/C compressor out of operation range | 0 | 1 |  |  | 1.23
1555 | 1554 | Active alarm 1055 |  | 0 | 1
1556 | 1555 | Active alarm 1056 |  | 0 | 1
1557 | 1556 | Active alarm 1057 |  | 0 | 1
1558 | 1557 | Active alarm 1058 |  | 0 | 1
1559 | 1558 | Active alarm 1059 | Alarm 71:9 H/C expansion valve controller com. Error | 0 | 1 |  |  | 1.23
1560 | 1559 | Active alarm 1060 |  | 0 | 1
1561 | 1560 | Active alarm 1061 |  | 0 | 1
1562 | 1561 | Active alarm 1062 |  | 0 | 1
1563 | 1562 | Active alarm 1063 |  | 0 | 1
1564 | 1563 | Active alarm 1064 |  | 0 | 1
1565 | 1564 | Active alarm 1065 |  | 0 | 1
1566 | 1565 | Active alarm 1066 | Alarm 72:1 H/C high pressure switch tripped | 0 | 1 |  |  | 1.23
1567 | 1566 | Active alarm 1067 | Alarm 72:2 H/C high pressure above alarm limit | 0 | 1 |  |  | 1.23
1568 | 1567 | Active alarm 1068 | Alarm 72:3 H/C thermal switch compressor no. 1 tripped | 0 | 1 |  |  | 2.46
1569 | 1568 | Active alarm 1069 | Alarm 72:4 H/C discharge temperature above alarm limit | 0 | 1 |  |  | 1.23
1570 | 1569 | Active alarm 1070 | Alarm 72:5 H/C discharge temperature sensor defective | 0 | 1 |  |  | 1.23
1571 | 1570 | Active alarm 1071 | Alarm 72:6 H/C high pressure sensor defective | 0 | 1 |  |  | 1.23
1572 | 1571 | Active alarm 1072 | Alarm 72:7 H/C low pressure sensor defective | 0 | 1 |  |  | 1.23
1573 | 1572 | Active alarm 1073 | Alarm 72:8 H/C suction temperature sensor defective | 0 | 1 |  |  | 1.23
1574 | 1573 | Active alarm 1074 | Alarm 72:9 H/C pressure difference below alarm limit | 0 | 1 |  |  | 1.23
1575 | 1574 | Active alarm 1075 | Alarm 72:10 H/C maintenance and compressor | 0 | 1 |  |  | 1.23
1576 | 1575 | Active alarm 1076 | Alarm 72:11 H/C superheat temperature below alarm limit | 0 | 1 |  |  | 1.23
1577 | 1576 | Active alarm 1077 | Alarm 72:12 H/C unloading of low pressure | 0 | 1 |  |  | 1.23
1578 | 1577 | Active alarm 1078 | Alarm 72:13 H/C unloading of high pressure | 0 | 1 |  |  | 1.23
1579 | 1578 | Active alarm 1079 | Alarm 72:14 H/C low pressure below alarm limit | 0 | 1 |  |  | 1.23
1580 | 1579 | Active alarm 1080 | Alarm 72:15 H/C thermal switch compressor no. 2 tripped | 0 | 1 |  |  | 2.46
1581 | 1580 | Active alarm 1081 |  | 0 | 1
1582 | 1581 | Active alarm 1082 |  | 0 | 1
1583 | 1582 | Active alarm 1083 |  | 0 | 1
1584 | 1583 | Active alarm 1084 |  | 0 | 1
1585 | 1584 | Active alarm 1085 |  | 0 | 1
1586 | 1585 | Active alarm 1086 |  | 0 | 1
1587 | 1586 | Active alarm 1087 |  | 0 | 1
1588 | 1587 | Active alarm 1088 |  | 0 | 1
1589 | 1588 | Active alarm 1089 |  | 0 | 1
1590 | 1589 | Active alarm 1090 |  | 0 | 1
1591 | 1590 | Active alarm 1091 |  | 0 | 1
1592 | 1591 | Active alarm 1092 |  | 0 | 1
1593 | 1592 | Active alarm 1093 |  | 0 | 1
1594 | 1593 | Active alarm 1094 |  | 0 | 1
1595 | 1594 | Active alarm 1095 |  | 0 | 1
1596 | 1595 | Active alarm 1096 |  | 0 | 1
1597 | 1596 | Active alarm 1097 |  | 0 | 1
1598 | 1597 | Active alarm 1098 |  | 0 | 1
1599 | 1598 | Active alarm 1099 |  | 0 | 1
1600 | 1599 | Active alarm 1100 |  | 0 | 1
1601 | 1600 | Active alarm 1101 |  | 0 | 1
1602 | 1601 | Active alarm 1102 |  | 0 | 1
1603 | 1602 | Active alarm 1103 |  | 0 | 1
1604 | 1603 | Active alarm 1104 |  | 0 | 1
1605 | 1604 | Active alarm 1105 |  | 0 | 1
1606 | 1605 | Active alarm 1106 |  | 0 | 1
1607 | 1606 | Active alarm 1107 |  | 0 | 1
1608 | 1607 | Active alarm 1108 |  | 0 | 1
1609 | 1608 | Active alarm 1109 |  | 0 | 1
1610 | 1609 | Active alarm 1110 |  | 0 | 1
1611 | 1610 | Active alarm 1111 |  | 0 | 1
1612 | 1611 | Active alarm 1112 |  | 0 | 1
1613 | 1612 | Active alarm 1113 |  | 0 | 1
1614 | 1613 | Active alarm 1114 |  | 0 | 1
1615 | 1614 | Active alarm 1115 |  | 0 | 1
1616 | 1615 | Active alarm 1116 |  | 0 | 1
1617 | 1616 | Active alarm 1117 |  | 0 | 1
1618 | 1617 | Active alarm 1118 |  | 0 | 1
1619 | 1618 | Active alarm 1119 |  | 0 | 1
1620 | 1619 | Active alarm 1120 |  | 0 | 1
1621 | 1620 | Active alarm 1121 |  | 0 | 1
1622 | 1621 | Active alarm 1122 |  | 0 | 1
1623 | 1622 | Active alarm 1123 |  | 0 | 1
1624 | 1623 | Active alarm 1124 |  | 0 | 1
1625 | 1624 | Active alarm 1125 |  | 0 | 1
1626 | 1625 | Active alarm 1126 |  | 0 | 1
1627 | 1626 | Active alarm 1127 |  | 0 | 1
1628 | 1627 | Active alarm 1128 |  | 0 | 1
1629 | 1628 | Active alarm 1129 |  | 0 | 1
1630 | 1629 | Active alarm 1130 |  | 0 | 1
1631 | 1630 | Active alarm 1131 |  | 0 | 1
1632 | 1631 | Active alarm 1132 |  | 0 | 1
1633 | 1632 | Active alarm 1133 |  | 0 | 1
1634 | 1633 | Active alarm 1134 |  | 0 | 1
1635 | 1634 | Active alarm 1135 |  | 0 | 1
1636 | 1635 | Active alarm 1136 |  | 0 | 1
1637 | 1636 | Active alarm 1137 |  | 0 | 1
1638 | 1637 | Active alarm 1138 |  | 0 | 1
1639 | 1638 | Active alarm 1139 |  | 0 | 1
1640 | 1639 | Active alarm 1140 |  | 0 | 1
1641 | 1640 | Active alarm 1141 |  | 0 | 1
1642 | 1641 | Active alarm 1142 | Alarm 77:2 MIRU 1 motor controller over current | 0 | 1 |  |  | 1.25
1643 | 1642 | Active alarm 1143 | Alarm 77:3 MIRU 1 motor controller under voltage | 0 | 1 |  |  | 1.25
1644 | 1643 | Active alarm 1144 | Alarm 77:4 MIRU 1 motor controller over voltage | 0 | 1 |  |  | 1.25
1645 | 1644 | Active alarm 1145 | Alarm 77:5 MIRU 1 motor controller over temperature | 0 | 1 |  |  | 1.25
1646 | 1645 | Active alarm 1146 | Alarm 77:6 MIRU 1 motor controller start error | 0 | 1 |  |  | 1.25
1647 | 1646 | Active alarm 1147 | Alarm 77:7 MIRU 1 motor controller ripple error | 0 | 1 |  |  | 1.25
1648 | 1647 | Active alarm 1148 | Alarm 77:8 MIRU 1 motor controller phase error | 0 | 1 |  |  | 1.25
1649 | 1648 | Active alarm 1149 | Alarm 77:9 MIRU 1 motor controller internal memory error | 0 | 1 |  |  | 1.25
1650 | 1649 | Active alarm 1150 | Alarm 77:10 MIRU 1 motor controller current reduction | 0 | 1 |  |  | 1.25
1651 | 1650 | Active alarm 1151 | Alarm 77:11 MIRU 1 motor controller internal com. error | 0 | 1 |  |  | 1.25
1652 | 1651 | Active alarm 1152 |  | 0 | 1
1653 | 1652 | Active alarm 1153 |  | 0 | 1
1654 | 1653 | Active alarm 1154 |  | 0 | 1
1655 | 1654 | Active alarm 1155 |  | 0 | 1
1656 | 1655 | Active alarm 1156 |  | 0 | 1
1657 | 1656 | Active alarm 1157 | Alarm 78:2 MIRU 2 motor controller over current | 0 | 1 |  |  | 1.25
1658 | 1657 | Active alarm 1158 | Alarm 78:3 MIRU 2 motor controller under voltage | 0 | 1 |  |  | 1.25
1659 | 1658 | Active alarm 1159 | Alarm 78:4 MIRU 2 motor controller over voltage | 0 | 1 |  |  | 1.25
1660 | 1659 | Active alarm 1160 | Alarm 78:5 MIRU 2 motor controller over temperature | 0 | 1 |  |  | 1.25
1661 | 1660 | Active alarm 1161 | Alarm 78:6 MIRU 2 motor controller start error | 0 | 1 |  |  | 1.25
1662 | 1661 | Active alarm 1162 | Alarm 78:7 MIRU 2 motor controller ripple error | 0 | 1 |  |  | 1.25
1663 | 1662 | Active alarm 1163 | Alarm 78:8 MIRU 2 motor controller phase error | 0 | 1 |  |  | 1.25
1664 | 1663 | Active alarm 1164 | Alarm 78:9 MIRU 2 motor controller internal memory error | 0 | 1 |  |  | 1.25
1665 | 1664 | Active alarm 1165 | Alarm 78:10 MIRU 2 motor controller current reduction | 0 | 1 |  |  | 1.25
1666 | 1665 | Active alarm 1166 | Alarm 78:11 MIRU 2 motor controller internal com. error | 0 | 1 |  |  | 1.25
1667 | 1666 | Active alarm 1167 |  | 0 | 1
1668 | 1667 | Active alarm 1168 |  | 0 | 1
1669 | 1668 | Active alarm 1169 |  | 0 | 1
1670 | 1669 | Active alarm 1170 |  | 0 | 1
1671 | 1670 | Active alarm 1171 |  | 0 | 1
1672 | 1671 | Active alarm 1172 | Alarm 79:2 MIRU 3 motor controller over current | 0 | 1 |  |  | 1.25
1673 | 1672 | Active alarm 1173 | Alarm 79:3 MIRU 3 motor controller under voltage | 0 | 1 |  |  | 1.25
1674 | 1673 | Active alarm 1174 | Alarm 79:4 MIRU 3 motor controller over voltage | 0 | 1 |  |  | 1.25
1675 | 1674 | Active alarm 1175 | Alarm 79:5 MIRU 3 motor controller over temperature | 0 | 1 |  |  | 1.25
1676 | 1675 | Active alarm 1176 | Alarm 79:6 MIRU 3 motor controller start error | 0 | 1 |  |  | 1.25
1677 | 1676 | Active alarm 1177 | Alarm 79:7 MIRU 3 motor controller ripple error | 0 | 1 |  |  | 1.25
1678 | 1677 | Active alarm 1178 | Alarm 79:8 MIRU 3 motor controller phase error | 0 | 1 |  |  | 1.25
1679 | 1678 | Active alarm 1179 | Alarm 79:9 MIRU 3 motor controller internal memory error | 0 | 1 |  |  | 1.25
1680 | 1679 | Active alarm 1180 | Alarm 79:10 MIRU 3 motor controller current reduction | 0 | 1 |  |  | 1.25
1681 | 1680 | Active alarm 1181 | Alarm 79:11 MIRU 3 motor controller internal com. error | 0 | 1 |  |  | 1.25
1682 | 1681 | Active alarm 1182 |  | 0 | 1
1683 | 1682 | Active alarm 1183 |  | 0 | 1
1684 | 1683 | Active alarm 1184 |  | 0 | 1
1685 | 1684 | Active alarm 1185 |  | 0 | 1
1686 | 1685 | Active alarm 1186 |  | 0 | 1
1687 | 1686 | Active alarm 1187 |  | 0 | 1
1688 | 1687 | Active alarm 1188 |  | 0 | 1
1689 | 1688 | Active alarm 1189 |  | 0 | 1
1690 | 1689 | Active alarm 1190 |  | 0 | 1
1691 | 1690 | Active alarm 1191 |  | 0 | 1
1692 | 1691 | Active alarm 1192 |  | 0 | 1
1693 | 1692 | Active alarm 1193 |  | 0 | 1
1694 | 1693 | Active alarm 1194 |  | 0 | 1
1695 | 1694 | Active alarm 1195 |  | 0 | 1
1696 | 1695 | Active alarm 1196 |  | 0 | 1
1697 | 1696 | Active alarm 1197 |  | 0 | 1
1698 | 1697 | Active alarm 1198 |  | 0 | 1
1699 | 1698 | Active alarm 1199 |  | 0 | 1
1700 | 1699 | Active alarm 1200 |  | 0 | 1
1701 | 1700 | Active alarm 1201 |  | 0 | 1
1702 | 1701 | Active alarm 1202 | Alarm 81:2 SMART Link no. 1 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1703 | 1702 | Active alarm 1203 | Alarm 81:3 SMART Link no. 1 High pressure switch tripped | 0 | 1 |  |  | 1.27
1704 | 1703 | Active alarm 1204 | Alarm 81:4 SMART Link no. 1 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1705 | 1704 | Active alarm 1205 | Alarm 81:5 SMART Link no. 1 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1706 | 1705 | Active alarm 1206 | Alarm 81:6 SMART Link no. 1 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1707 | 1706 | Active alarm 1207 | Alarm 81:7 SMART Link no. 1 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1708 | 1707 | Active alarm 1208 | Alarm 81:8 SMART Link no. 1 Envelope alarm | 0 | 1 |  |  | 1.27
1709 | 1708 | Active alarm 1209 | Alarm 81:9 SMART Link no. 1 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1710 | 1709 | Active alarm 1210 | Alarm 81:10 SMART Link no. 1 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1711 | 1710 | Active alarm 1211 | Alarm 81:11 SMART Link no. 1 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1712 | 1711 | Active alarm 1212 |  | 0 | 1
1713 | 1712 | Active alarm 1213 |  | 0 | 1
1714 | 1713 | Active alarm 1214 |  | 0 | 1
1715 | 1714 | Active alarm 1215 |  | 0 | 1
1716 | 1715 | Active alarm 1216 |  | 0 | 1
1717 | 1716 | Active alarm 1217 | Alarm 82:2 SMART Link no. 2 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1718 | 1717 | Active alarm 1218 | Alarm 82:3 SMART Link no. 2 High pressure switch tripped | 0 | 1 |  |  | 1.27
1719 | 1718 | Active alarm 1219 | Alarm 82:4 SMART Link no. 2 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1720 | 1719 | Active alarm 1220 | Alarm 82:5 SMART Link no. 2 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1721 | 1720 | Active alarm 1221 | Alarm 82:6 SMART Link no. 2 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1722 | 1721 | Active alarm 1222 | Alarm 82:7 SMART Link no. 2 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1723 | 1722 | Active alarm 1223 | Alarm 82:8 SMART Link no. 2 Envelope alarm | 0 | 1 |  |  | 1.27
1724 | 1723 | Active alarm 1224 | Alarm 82:9 SMART Link no. 2 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1725 | 1724 | Active alarm 1225 | Alarm 82:10 SMART Link no. 2 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1726 | 1725 | Active alarm 1226 | Alarm 82:11 SMART Link no. 2 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1727 | 1726 | Active alarm 1227 |  | 0 | 1
1728 | 1727 | Active alarm 1228 |  | 0 | 1
1729 | 1728 | Active alarm 1229 |  | 0 | 1
1730 | 1729 | Active alarm 1230 |  | 0 | 1
1731 | 1730 | Active alarm 1231 |  | 0 | 1
1732 | 1731 | Active alarm 1232 | Alarm 83:2 SMART Link no. 3 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1733 | 1732 | Active alarm 1233 | Alarm 83:3 SMART Link no. 3 High pressure switch tripped | 0 | 1 |  |  | 1.27
1734 | 1733 | Active alarm 1234 | Alarm 83:4 SMART Link no. 3 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1735 | 1734 | Active alarm 1235 | Alarm 83:5 SMART Link no. 3 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1736 | 1735 | Active alarm 1236 | Alarm 83:6 SMART Link no. 3 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1737 | 1736 | Active alarm 1237 | Alarm 83:7 SMART Link no. 3 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1738 | 1737 | Active alarm 1238 | Alarm 83:8 SMART Link no. 3 Envelope alarm | 0 | 1 |  |  | 1.27
1739 | 1738 | Active alarm 1239 | Alarm 83:9 SMART Link no. 3 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1740 | 1739 | Active alarm 1240 | Alarm 83:10 SMART Link no. 3 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1741 | 1740 | Active alarm 1241 | Alarm 83:11 SMART Link no. 3 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1742 | 1741 | Active alarm 1242 |  | 0 | 1
1743 | 1742 | Active alarm 1243 |  | 0 | 1
1744 | 1743 | Active alarm 1244 |  | 0 | 1
1745 | 1744 | Active alarm 1245 |  | 0 | 1
1746 | 1745 | Active alarm 1246 |  | 0 | 1
1747 | 1746 | Active alarm 1247 | Alarm 84:2 SMART Link no. 4 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1748 | 1747 | Active alarm 1248 | Alarm 84:3 SMART Link no. 4 High pressure switch tripped | 0 | 1 |  |  | 1.27
1749 | 1748 | Active alarm 1249 | Alarm 84:4 SMART Link no. 4 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1750 | 1749 | Active alarm 1250 | Alarm 84:5 SMART Link no. 4 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1751 | 1750 | Active alarm 1251 | Alarm 84:6 SMART Link no. 4 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1752 | 1751 | Active alarm 1252 | Alarm 84:7 SMART Link no. 4 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1753 | 1752 | Active alarm 1253 | Alarm 84:8 SMART Link no. 4 Envelope alarm | 0 | 1 |  |  | 1.27
1754 | 1753 | Active alarm 1254 | Alarm 84:9 SMART Link no. 4 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1755 | 1754 | Active alarm 1255 | Alarm 84:10 SMART Link no. 4 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1756 | 1755 | Active alarm 1256 | Alarm 84:11 SMART Link no. 4 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1757 | 1756 | Active alarm 1257 |  | 0 | 1
1758 | 1757 | Active alarm 1258 |  | 0 | 1
1759 | 1758 | Active alarm 1259 |  | 0 | 1
1760 | 1759 | Active alarm 1260 |  | 0 | 1
1761 | 1760 | Active alarm 1261 |  | 0 | 1
1762 | 1761 | Active alarm 1262 |  | 0 | 1
1763 | 1762 | Active alarm 1263 |  | 0 | 1
1764 | 1763 | Active alarm 1264 |  | 0 | 1
1765 | 1764 | Active alarm 1265 |  | 0 | 1
1766 | 1765 | Active alarm 1266 |  | 0 | 1
1767 | 1766 | Active alarm 1267 |  | 0 | 1
1768 | 1767 | Active alarm 1268 |  | 0 | 1
1769 | 1768 | Active alarm 1269 |  | 0 | 1
1770 | 1769 | Active alarm 1270 |  | 0 | 1
1771 | 1770 | Active alarm 1271 |  | 0 | 1
1772 | 1771 | Active alarm 1272 |  | 0 | 1
1773 | 1772 | Active alarm 1273 |  | 0 | 1
1774 | 1773 | Active alarm 1274 |  | 0 | 1
1775 | 1774 | Active alarm 1275 |  | 0 | 1
1776 | 1775 | Active alarm 1276 |  | 0 | 1
1777 | 1776 | Active alarm 1277 |  | 0 | 1
1778 | 1777 | Active alarm 1278 |  | 0 | 1
1779 | 1778 | Active alarm 1279 |  | 0 | 1
1780 | 1779 | Active alarm 1280 |  | 0 | 1
1781 | 1780 | Active alarm 1281 |  | 0 | 1
1782 | 1781 | Active alarm 1282 |  | 0 | 1
1783 | 1782 | Active alarm 1283 |  | 0 | 1
1784 | 1783 | Active alarm 1284 |  | 0 | 1
1785 | 1784 | Active alarm 1285 |  | 0 | 1
1786 | 1785 | Active alarm 1286 |  | 0 | 1
1787 | 1786 | Active alarm 1287 |  | 0 | 1
1788 | 1787 | Active alarm 1288 |  | 0 | 1
1789 | 1788 | Active alarm 1289 |  | 0 | 1
1790 | 1789 | Active alarm 1290 |  | 0 | 1
1791 | 1790 | Active alarm 1291 |  | 0 | 1
1792 | 1791 | Active alarm 1292 |  | 0 | 1
1793 | 1792 | Active alarm 1293 |  | 0 | 1
1794 | 1793 | Active alarm 1294 |  | 0 | 1
1795 | 1794 | Active alarm 1295 |  | 0 | 1
1796 | 1795 | Active alarm 1296 |  | 0 | 1
1797 | 1796 | Active alarm 1297 |  | 0 | 1
1798 | 1797 | Active alarm 1298 |  | 0 | 1
1799 | 1798 | Active alarm 1299 |  | 0 | 1
1800 | 1799 | Active alarm 1300 |  | 0 | 1
1801 | 1800 | Active alarm 1301 |  | 0 | 1
1802 | 1801 | Active alarm 1302 |  | 0 | 1
1803 | 1802 | Active alarm 1303 |  | 0 | 1
1804 | 1803 | Active alarm 1304 |  | 0 | 1
1805 | 1804 | Active alarm 1305 |  | 0 | 1
1806 | 1805 | Active alarm 1306 |  | 0 | 1
1807 | 1806 | Active alarm 1307 |  | 0 | 1
1808 | 1807 | Active alarm 1308 |  | 0 | 1
1809 | 1808 | Active alarm 1309 |  | 0 | 1
1810 | 1809 | Active alarm 1310 |  | 0 | 1
1811 | 1810 | Active alarm 1311 |  | 0 | 1
1812 | 1811 | Active alarm 1312 |  | 0 | 1
1813 | 1812 | Active alarm 1313 |  | 0 | 1
1814 | 1813 | Active alarm 1314 |  | 0 | 1
1815 | 1814 | Active alarm 1315 |  | 0 | 1
1816 | 1815 | Active alarm 1316 |  | 0 | 1
1817 | 1816 | Active alarm 1317 |  | 0 | 1
1818 | 1817 | Active alarm 1318 |  | 0 | 1
1819 | 1818 | Active alarm 1319 |  | 0 | 1
1820 | 1819 | Active alarm 1320 |  | 0 | 1
1821 | 1820 | Active alarm 1321 |  | 0 | 1
1822 | 1821 | Active alarm 1322 |  | 0 | 1
1823 | 1822 | Active alarm 1323 |  | 0 | 1
1824 | 1823 | Active alarm 1324 |  | 0 | 1
1825 | 1824 | Active alarm 1325 |  | 0 | 1
1826 | 1825 | Active alarm 1326 |  | 0 | 1
1827 | 1826 | Active alarm 1327 |  | 0 | 1
1828 | 1827 | Active alarm 1328 |  | 0 | 1
1829 | 1828 | Active alarm 1329 |  | 0 | 1
1830 | 1829 | Active alarm 1330 |  | 0 | 1
1831 | 1830 | Active alarm 1331 |  | 0 | 1
1832 | 1831 | Active alarm 1332 |  | 0 | 1
1833 | 1832 | Active alarm 1333 |  | 0 | 1
1834 | 1833 | Active alarm 1334 |  | 0 | 1
1835 | 1834 | Active alarm 1335 |  | 0 | 1
1836 | 1835 | Active alarm 1336 |  | 0 | 1
1837 | 1836 | Active alarm 1337 |  | 0 | 1
1838 | 1837 | Active alarm 1338 |  | 0 | 1
1839 | 1838 | Active alarm 1339 |  | 0 | 1
1840 | 1839 | Active alarm 1340 |  | 0 | 1
1841 | 1840 | Active alarm 1341 |  | 0 | 1
1842 | 1841 | Active alarm 1342 |  | 0 | 1
1843 | 1842 | Active alarm 1343 |  | 0 | 1
1844 | 1843 | Active alarm 1344 |  | 0 | 1
1845 | 1844 | Active alarm 1345 |  | 0 | 1
1846 | 1845 | Active alarm 1346 |  | 0 | 1
1847 | 1846 | Active alarm 1347 |  | 0 | 1
1848 | 1847 | Active alarm 1348 |  | 0 | 1
1849 | 1848 | Active alarm 1349 |  | 0 | 1
1850 | 1849 | Active alarm 1350 |  | 0 | 1
1851 | 1850 | Active alarm 1351 |  | 0 | 1
1852 | 1851 | Active alarm 1352 |  | 0 | 1
1853 | 1852 | Active alarm 1353 |  | 0 | 1
1854 | 1853 | Active alarm 1354 |  | 0 | 1
1855 | 1854 | Active alarm 1355 |  | 0 | 1
1856 | 1855 | Active alarm 1356 |  | 0 | 1
1857 | 1856 | Active alarm 1357 |  | 0 | 1
1858 | 1857 | Active alarm 1358 |  | 0 | 1
1859 | 1858 | Active alarm 1359 |  | 0 | 1
1860 | 1859 | Active alarm 1360 |  | 0 | 1
1861 | 1860 | Active alarm 1361 |  | 0 | 1
1862 | 1861 | Active alarm 1362 |  | 0 | 1
1863 | 1862 | Active alarm 1363 |  | 0 | 1
1864 | 1863 | Active alarm 1364 |  | 0 | 1
1865 | 1864 | Active alarm 1365 |  | 0 | 1
1866 | 1865 | Active alarm 1366 |  | 0 | 1
1867 | 1866 | Active alarm 1367 |  | 0 | 1
1868 | 1867 | Active alarm 1368 |  | 0 | 1
1869 | 1868 | Active alarm 1369 |  | 0 | 1
1870 | 1869 | Active alarm 1370 |  | 0 | 1
1871 | 1870 | Active alarm 1371 |  | 0 | 1
1872 | 1871 | Active alarm 1372 |  | 0 | 1
1873 | 1872 | Active alarm 1373 |  | 0 | 1
1874 | 1873 | Active alarm 1374 |  | 0 | 1
1875 | 1874 | Active alarm 1375 |  | 0 | 1
1876 | 1875 | Active alarm 1376 |  | 0 | 1
1877 | 1876 | Active alarm 1377 |  | 0 | 1
1878 | 1877 | Active alarm 1378 |  | 0 | 1
1879 | 1878 | Active alarm 1379 |  | 0 | 1
1880 | 1879 | Active alarm 1380 |  | 0 | 1
1881 | 1880 | Active alarm 1381 |  | 0 | 1
1882 | 1881 | Active alarm 1382 |  | 0 | 1
1883 | 1882 | Active alarm 1383 |  | 0 | 1
1884 | 1883 | Active alarm 1384 |  | 0 | 1
1885 | 1884 | Active alarm 1385 |  | 0 | 1
1886 | 1885 | Active alarm 1386 |  | 0 | 1
1887 | 1886 | Active alarm 1387 |  | 0 | 1
1888 | 1887 | Active alarm 1388 |  | 0 | 1
1889 | 1888 | Active alarm 1389 |  | 0 | 1
1890 | 1889 | Active alarm 1390 |  | 0 | 1
1891 | 1890 | Active alarm 1391 |  | 0 | 1
1892 | 1891 | Active alarm 1392 |  | 0 | 1
1893 | 1892 | Active alarm 1393 |  | 0 | 1
1894 | 1893 | Active alarm 1394 |  | 0 | 1
1895 | 1894 | Active alarm 1395 |  | 0 | 1
1896 | 1895 | Active alarm 1396 |  | 0 | 1
1897 | 1896 | Active alarm 1397 |  | 0 | 1
1898 | 1897 | Active alarm 1398 |  | 0 | 1
1899 | 1898 | Active alarm 1399 |  | 0 | 1
1900 | 1899 | Active alarm 1400 |  | 0 | 1
1901 | 1900 | Active alarm 1401 |  | 0 | 1
1902 | 1901 | Active alarm 1402 |  | 0 | 1
1903 | 1902 | Active alarm 1403 |  | 0 | 1
1904 | 1903 | Active alarm 1404 |  | 0 | 1
1905 | 1904 | Active alarm 1405 |  | 0 | 1
1906 | 1905 | Active alarm 1406 |  | 0 | 1
1907 | 1906 | Active alarm 1407 |  | 0 | 1
1908 | 1907 | Active alarm 1408 |  | 0 | 1
1909 | 1908 | Active alarm 1409 |  | 0 | 1
1910 | 1909 | Active alarm 1410 |  | 0 | 1
1911 | 1910 | Active alarm 1411 | Alarm 95:1 Supply air pre filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1912 | 1911 | Active alarm 1412 | Alarm 95:2 Extract air pre filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1913 | 1912 | Active alarm 1413 | Alarm 95:3 Supply air AHU filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1914 | 1913 | Active alarm 1414 | Alarm 95:4 Extract air AHU filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1915 | 1914 | Active alarm 1415 | Alarm 95:5 End filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1916 | 1915 | Active alarm 1416 |  | 0 | 1
1917 | 1916 | Active alarm 1417 |  | 0 | 1
1918 | 1917 | Active alarm 1418 |  | 0 | 1
1919 | 1918 | Active alarm 1419 |  | 0 | 1
1920 | 1919 | Active alarm 1420 |  | 0 | 1
1921 | 1920 | Active alarm 1421 |  | 0 | 1
1922 | 1921 | Active alarm 1422 |  | 0 | 1
1923 | 1922 | Active alarm 1423 |  | 0 | 1
1924 | 1923 | Active alarm 1424 | Info 95:14 Reduced humidity recovery time above alarm limit | 0 | 1 |  |  | 2.43
1925 | 1924 | Active alarm 1425 | Info 95:15 Supply air humidity level above outdoor air level | 0 | 1 |  |  | 2.43
1926 | 1925 | Active alarm 1426 | Alarm 96:1 H/C defrost calibration not performed | 0 | 1 |  |  | 1.27
1927 | 1926 | Active alarm 1427 | Alarm 96:2 H/C defrost calibration not approved | 0 | 1 |  |  | 1.27
1928 | 1927 | Active alarm 1428 | Alarm 96:3 H/C minimum SA flow limit below factory setting | 0 | 1 |  |  | 1.27
1929 | 1928 | Active alarm 1429 | Alarm 96:4 H/C minimum EA flow limit below factory setting | 0 | 1 |  |  | 1.27
1930 | 1929 | Active alarm 1430 | Alarm 96:5 H/C OA temp limit for heating below factory setting | 0 | 1 |  |  | 1.27
1931 | 1930 | Active alarm 1431 |  | 0 | 1
1932 | 1931 | Active alarm 1432 |  | 0 | 1
1933 | 1932 | Active alarm 1433 |  | 0 | 1
1934 | 1933 | Active alarm 1434 |  | 0 | 1
1935 | 1934 | Active alarm 1435 |  | 0 | 1
1936 | 1935 | Active alarm 1436 |  | 0 | 1
1937 | 1936 | Active alarm 1437 |  | 0 | 1
1938 | 1937 | Active alarm 1438 |  | 0 | 1
1939 | 1938 | Active alarm 1439 |  | 0 | 1
1940 | 1939 | Active alarm 1440 |  | 0 | 1
1941 | 1940 | Active alarm 1441 | Info 97:1 Cloud connection offline | 0 | 1 |  |  | 2.42
1942 | 1941 | Active alarm 1442 | Info 97:2 Cloud certificate missing/expired | 0 | 1 |  |  | 2.42
1943 | 1942 | Active alarm 1443 |  | 0 | 1
1944 | 1943 | Active alarm 1444 |  | 0 | 1
1945 | 1944 | Active alarm 1445 |  | 0 | 1
1946 | 1945 | Active alarm 1446 |  | 0 | 1
1947 | 1946 | Active alarm 1447 |  | 0 | 1
1948 | 1947 | Active alarm 1448 |  | 0 | 1
1949 | 1948 | Active alarm 1449 |  | 0 | 1
1950 | 1949 | Active alarm 1450 |  | 0 | 1
1951 | 1950 | Active alarm 1451 |  | 0 | 1
1952 | 1951 | Active alarm 1452 | Info 97:12 Plate heat exchanger bypass optimization not performed | 0 | 1 |  |  | 1.13
1953 | 1952 | Active alarm 1453 | Info 97:13 Plate heat exchanger bypass optimization not approved | 0 | 1 |  |  | 1.13
1954 | 1953 | Active alarm 1454 | Info 97:14 Plate heat exchanger defrost calibration not performed | 0 | 1 |  |  | 1.13
1955 | 1954 | Active alarm 1455 | Info 97:15 Plate heat exchanger defrost calibration not approved | 0 | 1 |  |  | 1.13
1956 | 1955 | Active alarm 1456 | Info 98:1 Supply air pre-filter calibration not performed | 0 | 1
1957 | 1956 | Active alarm 1457 | Info 98:2 Supply air pre-filter calibration not approved | 0 | 1
1958 | 1957 | Active alarm 1458 | Info 98:3 Extract air pre-filter calibration not performed | 0 | 1
1959 | 1958 | Active alarm 1459 | Info 98:4 Extract air pre-filter calibration not approved | 0 | 1
1960 | 1959 | Active alarm 1460 | Info 98:5 Supply air air handling unit filter calibration not performed | 0 | 1
1961 | 1960 | Active alarm 1461 | Info 98:6 Supply air air handling unit filter calibration not approved | 0 | 1
1962 | 1961 | Active alarm 1462 | Info 98:7 Extract air air handling unit filter calibration not performed | 0 | 1
1963 | 1962 | Active alarm 1463 | Info 98:8 Extract air air handling unit filter calibration not approved | 0 | 1
1964 | 1963 | Active alarm 1464 | Info 98:9 Supply air end filter calibration not performed | 0 | 1
1965 | 1964 | Active alarm 1465 | Info 98:10 Supply air end filter calibration not approved | 0 | 1
1966 | 1965 | Active alarm 1466 | Info 98:11 Rotary heat exchanger defrost calibration not performed | 0 | 1
1967 | 1966 | Active alarm 1467 | Info 98:12 Rotary heat exchanger defrost calibration not approved | 0 | 1
1968 | 1967 | Active alarm 1468 | Info 98:13 ReCO2 calibration not performed | 0 | 1
1969 | 1968 | Active alarm 1469 | Info 98:14 ReCO2 calibration not approved | 0 | 1
1970 | 1969 | Active alarm 1470 | Info 98:15 ReCO2 incorrect setting | 0 | 1
1971 | 1970 | Active alarm 1471 | Info 99:1 E-mail error | 0 | 1
1972 | 1971 | Active alarm 1472 |  | 0 | 1
1973 | 1972 | Active alarm 1473 |  | 0 | 1
1974 | 1973 | Active alarm 1474 |  | 0 | 1
1975 | 1974 | Active alarm 1475 | Info 99:5 FTP error | 0 | 1 |  |  | 1.19
1976 | 1975 | Active alarm 1476 | Info 99:6 Schedule invalid data auto corrected | 0 | 1 |  |  | 2.36
1977 | 1976 | Active alarm 1477 | Info 99:7 SD card memory soon full. Oldest log data will soon be deleted | 0 | 1
1978 | 1977 | Active alarm 1478 | Info 99:8 SD card memory full. Oldest log data deleted | 0 | 1
1979 | 1978 | Active alarm 1479 | Info 99:9 IQlogic CPU2 reboot caused by corrupt SD card remove and replace | 0 | 1 |  |  | 2.42
1980 | 1979 | Active alarm 1480 |  | 0 | 1
1981 | 1980 | Active alarm 1481 | Info 99:11 No external outdoor air temperature sensor connected for heat retention | 0 | 1 |  |  | 1.26
1982 | 1981 | Active alarm 1482 | Info 99:12 No extract air/room temperature sensor connected | 0 | 1 |  |  | 1.32
1983 | 1982 | Active alarm 1483 |  | 0 | 1
1984 | 1983 | Active alarm 1484 | Info 99:14 Internal serial memory error CPU 1 | 0 | 1
1985 | 1984 | Active alarm 1485 | Info 99:15 Clock circuit defective | 0 | 1
1986 | 1985 | Active alarm 1486 |  | 0 | 1
1987 | 1986 | Active alarm 1487 |  | 0 | 1
1988 | 1987 | Active alarm 1488 |  | 0 | 1
1989 | 1988 | Active alarm 1489 |  | 0 | 1
1990 | 1989 | Active alarm 1490 |  | 0 | 1
1991 | 1990 | Active alarm 1491 |  | 0 | 1
1992 | 1991 | Active alarm 1492 |  | 0 | 1
1993 | 1992 | Active alarm 1493 |  | 0 | 1
1994 | 1993 | Active alarm 1494 |  | 0 | 1
1995 | 1994 | Active alarm 1495 |  | 0 | 1
1996 | 1995 | Active alarm 1496 |  | 0 | 1
1997 | 1996 | Active alarm 1497 |  | 0 | 1
1998 | 1997 | Active alarm 1498 |  | 0 | 1
1999 | 1998 | Active alarm 1499 |  | 0 | 1
2000 | 1999 | Active alarm 1500 |  | 0 | 1
2001 | 2000 | Active alarm group 1 |  | 0 | 1
2002 | 2001 | Active alarm group 2 |  | 0 | 1
2003 | 2002 | Active alarm group 3 |  | 0 | 1
2004 | 2003 | Active alarm group 4 |  | 0 | 1
2005 | 2004 | Active alarm group 5 |  | 0 | 1
2006 | 2005 | Active alarm group 6 |  | 0 | 1
2007 | 2006 | Active alarm group 7 |  | 0 | 1
2008 | 2007 | Active alarm group 8 |  | 0 | 1
2009 | 2008 | Active alarm group 9 |  | 0 | 1
2010 | 2009 | Active alarm group 10 |  | 0 | 1
2011 | 2010 | Active alarm group 11 |  | 0 | 1
2012 | 2011 | Active alarm group 12 |  | 0 | 1
2013 | 2012 | Active alarm group 13 |  | 0 | 1
2014 | 2013 | Active alarm group 14 |  | 0 | 1
2015 | 2014 | Active alarm group 15 |  | 0 | 1
2016 | 2015 | Active alarm group 16 |  | 0 | 1
2017 | 2016 | Active alarm group 17 |  | 0 | 1
2018 | 2017 | Active alarm group 18 |  | 0 | 1
2019 | 2018 | Active alarm group 19 |  | 0 | 1
2020 | 2019 | Active alarm group 20 |  | 0 | 1
2021 | 2020 | Active alarm group 21 |  | 0 | 1
2022 | 2021 | Active alarm group 22 |  | 0 | 1
2023 | 2022 | Active alarm group 23 |  | 0 | 1
2024 | 2023 | Active alarm group 24 |  | 0 | 1
2025 | 2024 | Active alarm group 25 |  | 0 | 1
2026 | 2025 | Active alarm group 26 |  | 0 | 1
2027 | 2026 | Active alarm group 27 |  | 0 | 1
2028 | 2027 | Active alarm group 28 |  | 0 | 1
2029 | 2028 | Active alarm group 29 |  | 0 | 1
2030 | 2029 | Active alarm group 30 |  | 0 | 1
2031 | 2030 | Active alarm group 31 |  | 0 | 1
2032 | 2031 | Active alarm group 32 |  | 0 | 1
2033 | 2032 | Active alarm group 33 |  | 0 | 1
2034 | 2033 | Active alarm group 34 |  | 0 | 1
2035 | 2034 | Active alarm group 35 |  | 0 | 1
2036 | 2035 | Active alarm group 36 |  | 0 | 1
2037 | 2036 | Active alarm group 37 |  | 0 | 1
2038 | 2037 | Active alarm group 38 |  | 0 | 1
2039 | 2038 | Active alarm group 39 |  | 0 | 1
2040 | 2039 | Active alarm group 40 |  | 0 | 1
2041 | 2040 | Active alarm group 41 |  | 0 | 1
2042 | 2041 | Active alarm group 42 |  | 0 | 1
2043 | 2042 | Active alarm group 43 |  | 0 | 1
2044 | 2043 | Active alarm group 44 |  | 0 | 1
2045 | 2044 | Active alarm group 45 |  | 0 | 1
2046 | 2045 | Active alarm group 46 |  | 0 | 1
2047 | 2046 | Active alarm group 47 |  | 0 | 1
2048 | 2047 | Active alarm group 48 |  | 0 | 1
2049 | 2048 | Active alarm group 49 |  | 0 | 1
2050 | 2049 | Active alarm group 50 |  | 0 | 1
2051 | 2050 | Active alarm group 51 |  | 0 | 1
2052 | 2051 | Active alarm group 52 |  | 0 | 1
2053 | 2052 | Active alarm group 53 |  | 0 | 1
2054 | 2053 | Active alarm group 54 |  | 0 | 1
2055 | 2054 | Active alarm group 55 |  | 0 | 1
2056 | 2055 | Active alarm group 56 |  | 0 | 1
2057 | 2056 | Active alarm group 57 |  | 0 | 1
2058 | 2057 | Active alarm group 58 |  | 0 | 1
2059 | 2058 | Active alarm group 59 |  | 0 | 1
2060 | 2059 | Active alarm group 60 |  | 0 | 1
2061 | 2060 | Active alarm group 61 |  | 0 | 1
2062 | 2061 | Active alarm group 62 |  | 0 | 1
2063 | 2062 | Active alarm group 63 |  | 0 | 1
2064 | 2063 | Active alarm group 64 |  | 0 | 1
2065 | 2064 | Active alarm group 65 |  | 0 | 1
2066 | 2065 | Active alarm group 66 |  | 0 | 1
2067 | 2066 | Active alarm group 67 |  | 0 | 1
2068 | 2067 | Active alarm group 68 |  | 0 | 1
2069 | 2068 | Active alarm group 69 |  | 0 | 1
2070 | 2069 | Active alarm group 70 |  | 0 | 1
2071 | 2070 | Active alarm group 71 |  | 0 | 1
2072 | 2071 | Active alarm group 72 |  | 0 | 1
2073 | 2072 | Active alarm group 73 |  | 0 | 1
2074 | 2073 | Active alarm group 74 |  | 0 | 1
2075 | 2074 | Active alarm group 75 |  | 0 | 1
2076 | 2075 | Active alarm group 76 |  | 0 | 1
2077 | 2076 | Active alarm group 77 |  | 0 | 1
2078 | 2077 | Active alarm group 78 |  | 0 | 1
2079 | 2078 | Active alarm group 79 |  | 0 | 1
2080 | 2079 | Active alarm group 80 |  | 0 | 1
2081 | 2080 | Active alarm group 81 |  | 0 | 1
2082 | 2081 | Active alarm group 82 |  | 0 | 1
2083 | 2082 | Active alarm group 83 |  | 0 | 1
2084 | 2083 | Active alarm group 84 |  | 0 | 1
2085 | 2084 | Active alarm group 85 |  | 0 | 1
2086 | 2085 | Active alarm group 86 |  | 0 | 1
2087 | 2086 | Active alarm group 87 |  | 0 | 1
2088 | 2087 | Active alarm group 88 |  | 0 | 1
2089 | 2088 | Active alarm group 89 |  | 0 | 1
2090 | 2089 | Active alarm group 90 |  | 0 | 1
2091 | 2090 | Active alarm group 91 |  | 0 | 1
2092 | 2091 | Active alarm group 92 |  | 0 | 1
2093 | 2092 | Active alarm group 93 |  | 0 | 1
2094 | 2093 | Active alarm group 94 |  | 0 | 1
2095 | 2094 | Active alarm group 95 |  | 0 | 1
2096 | 2095 | Active alarm group 96 |  | 0 | 1
2097 | 2096 | Active alarm group 97 |  | 0 | 1
2098 | 2097 | Active alarm group 98 |  | 0 | 1
2099 | 2098 | Active alarm group 99 |  | 0 | 1
2100 | 2099 | Active alarm group 100 |  | 0 | 1

## Vpac 5 (RW)
GOLD_E_F_EXOline_250905
Real var. Vpac 5 (R/W).
Index | Cell nbr | Name | Description | Min | Max | Unit | Default | Misc
Air flow regulation
1 | 0
2 | 3
3 | 6 | SA low speed air flow set point | Supply air flow set point for the unit when running in low speed operation. | 0 | Vp5,5 | l/s
4 | 9 | EA low speed air flow set point | Extract air flow set point for the unit when running in low speed operation. | 0 | Vp5,6 | l/s
5 | 12 | SA high speed air flow set point | Supply air flow set point for the unit when running in high speed operation. | Vp5,3 | Vp5,7 | l/s
6 | 15 | EA high speed air flow set point | Extract air flow set point for the unit when running in high speed operation. | Vp5,4 | Vp5,8 | l/s
7 | 18 | SA max speed air flow set point bost | Supply air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Vp5,5 | Vp2,57 | l/s
8 | 21 | EA max speed air flow set point bost | Extract air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Vp5,6 | Vp2,58 | l/s
9 | 24 | SA regulation zone | Supply air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
10 | 27 | EA regulation zone | Extract air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
11 | 30 | SA regulation I-time | Supply air flow regulator affection setting. | 1 | 1800 | s | 30
12 | 33 | EA regulation I-time | Extract air flow regulator affection setting. | 1 | 1800 | s | 30
13 | 36
14 | 39
15 | 42
16 | 45
17 | 48
18 | 51
Pressure regulation
19 | 54 | SA low speed pressure set point | Supply air duct pressure set point for the unit when running in low speed operation. | 0.0 | Vp5,21 | Pa
20 | 57 | EA low speed pressure set point | Extract air duct pressure set point for the unit when running in low speed operation. | 0.0 | Vp5,22 | Pa
21 | 60 | SA high speed pressure set point | Supply air duct pressure for the unit when running in high speed operation. | Vp5,19 | Vp5,23 | Pa
22 | 63 | EA high speed pressure set point | Extract air duct pressure set point for the unit when running in high speed operation. | Vp5,20 | Vp5,24 | Pa
23 | 66 | SA max speed pressure set point | Supply air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Vp5,21 | 750.0 | Pa
24 | 69 | EA max speed pressure set point | Extract air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Vp5,22 | 750.0 | Pa
25 | 72 | SA max speed output signal | Max. limit for the supply air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
26 | 75 | EA max speed output signal | Max. limit for the extract air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
27 | 78 | SA pressure regulation zone | Supply air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 1 | 40.00 | % | 15
28 | 81 | EA pressure regulation zone | Extract air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 1 | 40.00 | % | 15
29 | 84 | SA pressure I-time | Supply air pressure regulator affection setting. | 0 | 1800 | s | 30
30 | 87 | EA pressure I-time | Extract air pressure regulator affection setting. | 0 | 1800 | s | 30
31 | 90
32 | 93
Demand regulation
33 | 96 | Demand low speed CO2 set point | Set point for the CO2 input signal for the unit when running in low speed operation. | 0 | 10000 | ppm | 1000 | 1.23
34 | 99 | Demand high speed CO2 set point | Set point for the CO2 input signal for the unit when running in high speed operation. | 0 | 10000 | ppm | 750 | 1.23
35 | 102 | Demand low speed VOC set point | Set point for the VOC input signal for the unit when running in low speed operation. | 0 | 10000 | ppm | 2500 | 1.23
36 | 105 | Demand high speed VOC set point | Set point for the VOC input signal for the unit when running in high speed operation. | 0 | 10000 | ppm | 1500 | 1.23
37 | 108 | Demand low speed set point | Set point for the 0..10V input signal for the unit when running in low speed operation. | 0.00 | 100.00 | % | 50.00 | 1.23
38 | 111 | Demand high speed set point | Set point for the 0..10V input signal for the unit when running in high speed operation. | 10.00 | 100.00 | % | 25.00 | 1.23
39 | 114 | SA min speed air flow set point | Supply air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Vp2,55 | Vp5,41 | l/s
40 | 117 | EA min speed air flow set point | Extract air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Vp2,56 | Vp5,42 | l/s
41 | 120 | SA max speed air flow set point demand | Supply air flow max limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Vp5,39 | Vp2,57 | l/s
42 | 123 | EA max speed air flow set point demand | Extract air flow max. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Vp5,40 | Vp2,58 | l/s
43 | 126 | Demand P-band | Demand regulator P-band setting. | 1.00 | 100.00 | % | 40.00 | 1.23
44 | 129 | Demand I-time | Demand regulator affection setting. | 1 | 1800 | s | 1200 | 1.23
45 | 132 | Demand CO2 P-band | Demand C02 regulator P-band setting. | 0 | 10000 | ppm | 600 | 1.23
46 | 135 | Demand VOC P-band | Demand VOC regulator P-band setting. | 0 | 10000 | ppm | 1000 | 1.23
47 | 138
48 | 141
49 | 144
Slave controlled regulation
50 | 147 | Slave offset factor |  | 50.00 | 200.00 | % | 0.00
51 | 150 | SA slave offset air flow |  | - Vp2,57 | Vp2,57 | l/s | 0 | 1.31
52 | 153 | EA slave offset air flow |  | - Vp2,58 | Vp2,58 | l/s | 0 | 1.31
Fans OA temp compensation
53 | 156
54 | 159 | Outdoor temp compensation X1 |  | -50.00 | Vp5,55 | °C | -20.00
55 | 162 | Outdoor temp compensation X2 |  | Vp5,54 | Vp5,56 | °C | -10.00
56 | 165 | Outdoor temp compensation X3 |  | Vp5,55 | Vp5,57 | °C | 10.00
57 | 168 | Outdoor temp compensation X4 |  | Vp5,56 | 50.00 | °C | 20.00
58 | 171 | Outdoor temp compensation Y1 SA air flow |  | Vp2,55 | Vp2,57 | l/s
59 | 174 | Outdoor temp compensation Y2 SA air flow |  | Vp2,55 | Vp2,57 | l/s
60 | 177 | Outdoor temp compensation Y3 SA air flow |  | Vp2,55 | Vp2,57 | l/s
61 | 180 | Outdoor temp compensation Y4 SA air flow |  | Vp2,55 | Vp2,57 | l/s
62 | 183 | Outdoor temp compensation Y1 EA air flow |  | Vp2,56 | Vp2,58 | l/s
63 | 186 | Outdoor temp compensation Y2 EA air flow |  | Vp2,56 | Vp2,58 | l/s
64 | 189 | Outdoor temp compensation Y3 EA air flow |  | Vp2,56 | Vp2,58 | l/s
65 | 192 | Outdoor temp compensation Y4 EA air flow |  | Vp2,56 | Vp2,58 | l/s
66 | 195 | Outdoor temp compensation Y1 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
67 | 198 | Outdoor temp compensation Y2 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
68 | 201 | Outdoor temp compensation Y3 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
69 | 204 | Outdoor temp compensation Y4 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
70 | 207 | Outdoor temp compensation Y1 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
71 | 210 | Outdoor temp compensation Y2 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
72 | 213 | Outdoor temp compensation Y3 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
73 | 216 | Outdoor temp compensation Y4 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
74 | 219
75 | 222
76 | 225
77 | 228
Fans down regulation
78 | 231
79 | 234 | Down regulation neutral zone |  | 0.00 | 10.00 | K | 0.00
80 | 237 | Down regulation P-band |  | 1.00 | 10.00 | K | 5.00
81 | 240 | Down regulation I-time |  | 1 | 1800 | s | 30
82 | 243
83 | 246
Fans in operation at active fire alarm
84 | 249
85 | 252 | SA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
86 | 255 | EA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
87 | 258
88 | 261 | SA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00
89 | 264 | EA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00
91 | 270 | SA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00
92 | 273 | EA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00
93 | 276
94 | 279
Filters
95 | 282
96 | 285
97 | 288 | SA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
98 | 291 | EA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
99 | 294
100 | 297
101 | 300
102 | 303 | [5 empty] | 0
103 | 306 | SA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
104 | 309 | EA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
105 | 312
106 | 315
107 | 318
108 | 321
109 | 324 | SA end-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
110 | 327
111 | 330
112 | 333
Seasonal controlled temperature regulation
113 | 336 | Seasonal controlled temperature regulation active |  | -20.00 | 40.00 | °C | 0.00 | 1.23
114 | 339 | Seasonal controlled temperature regulation inactive |  | -20.00 | 40.00 | °C | 20.00 | 1.23
115 | 342
116 | 345
ERS-1 reg.
117 | 348 | ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4 |  | 2
118 | 351 | ERS 1 diff | Supply air temp difference setting according to the diagram for ERS 1. | 1.00 | 7.00 | K | 2.00
119 | 354 | ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
120 | 357
121 | 360
ERS-2 reg.
122 | 363 | ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10.00 | Vp5,123 | °C | 15.00
123 | 366 | ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | Vp5,122 | Vp5,124 | °C | 20.00
124 | 369 | ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | Vp5,123 | Vp5,125 | °C | 22.00
125 | 372 | ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | Vp5,124 | 40.00 | °C | 24.00
126 | 375 | ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
127 | 378 | ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
128 | 381 | ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
129 | 384 | ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
130 | 387
131 | 390
SA Reg.
132 | 393 | SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
133 | 396
134 | 399
EA Reg.
135 | 402 | EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
136 | 405 | SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 30.00 | °C | 16.00
137 | 408 | SA max temp set point | Supply air max. set point during EA/room regulation mode. | 8.00 | 50.00 | °C | 28.00 | 1.18
138 | 411 | EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
139 | 414 | EA regultaion I-time |  | 1 | 1800 | s | 30
140 | 417
141 | 420
ORS Reg.
142 | 423 | ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | Vp5,143 | °C | -20.00
143 | 426 | ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | Vp5,142 | Vp5,144 | °C | -10.00
144 | 429 | ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | Vp5,143 | Vp5,145 | °C | 10.00
145 | 432 | ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | Vp5,144 | 50.00 | °C | 20.00
146 | 435 | ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
147 | 438 | ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
148 | 441 | ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
149 | 444 | ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
150 | 447
151 | 450
ORE Reg.
152 | 453 | ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | Vp5,153 | °C | -20.00
153 | 456 | ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | Vp5,152 | Vp5,154 | °C | -10.00
154 | 459 | ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | Vp5,153 | Vp5,155 | °C | 10.00
155 | 462 | ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | Vp5,154 | 50.00 | °C | 20.00
156 | 465 | ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
157 | 468 | ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
158 | 471 | ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
159 | 474 | ORE breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
160 | 477
161 | 480
AHU external sensors
162 | 483
163 | 486
164 | 489
165 | 492
166 | 495
167 | 498
168 | 501 | External room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
169 | 504 | External room temp from BMS alarm time |  | 0 | 9999 | min | 5
170 | 507
171 | 510
172 | 513
173 | 516
174 | 519
175 | 522
176 | 525
177 | 528
178 | 531 | External OA temp from BMS |  | -55.00 | 125.00 | °C | 0.00
179 | 534 | External OA temp from BMS alarm time |  | 0 | 9999 | min | 5
180 | 537
181 | 540
AHU Heat exchange
182 | 543
183 | 546
184 | 549 | RHX defrost start limit |  | 30.0 | 100.0 | Pa | 50.0
185 | 552
186 | 555
187 | 558
188 | 561 | RHX sorption rotor function | Moved to Vpac 6 index 188 | 0 | 2 |  | 0 | 1.13
189 | 564
190 | 567
191 | 570 | RHX min exhaust air temp set point |  | -40.00 | 20.00 | °C | 5.00
192 | 573 | RHX min exhaust air temp P-band |  | 1.00 | 40.00 | K | 8.00
193 | 576 | RHX min exhaust air temp I-time |  | 0 | 30000 | s | 30
194 | 579
195 | 582
196 | 585
197 | 588
198 | 591
199 | 594 | PHX periodic operation interval |  | 0 | 168 | h | 24
200 | 597 | PHX periodic operation time |  | 0 | 60 | min | 3
201 | 600
202 | 603
203 | 606
204 | 609
205 | 612
206 | 615
207 | 618 | CHX periodic operation interval |  | 0 | 168 | h | 24
208 | 621 | CHX periodic operation time |  | 0 | 60 | min | 3
209 | 624
210 | 627
211 | 630
212 | 633
213 | 636 | PHX/CHX Bypass defrost limit | PHX is default 3°C, CHX is default 5°C. | -10.00 | 5.00 | °C
214 | 639 | PHX/CHX Bypass defrost P-band |  | 1.00 | 40.00 | K | 20.00
215 | 642 | PHX/CHX Bypass defrost I-time |  | 1 | 600 | s | 60
216 | 645
217 | 648
218 | 651
219 | 654
220 | 657 | Heat exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00
221 | 660 | Heat exchange temperature regulation I-time |  | 1 | 1800 | s | 50
222 | 663 | Cool exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00 | 1.11
223 | 666 | Cool exchange temperature regulation I-time |  | 1 | 1800 | s | 50 | 1.11
224 | 669
225 | 672
AHU Heat/Cool
226 | 675 | Re-heat P-band |  | 1.00 | 10.00 | K | 8.00
227 | 678 | Re-heat I-time |  | 1 | 1800 | s | 70
228 | 681
229 | 684
230 | 687 | Re-heat periodic operation interval |  | 0 | 168 | h | 24
231 | 690 | Re-heat periodic operation time |  | 0 | 60 | min | 3
232 | 693
233 | 696
234 | 699
235 | 702
236 | 705
237 | 708
238 | 711
239 | 714 | Extra regulation sequence 1 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
240 | 717 | Extra regulation sequence 1 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
241 | 720 | Extra regulation sequence 1 heat P-band |  | 1.00 | 10.00 | K | 8
242 | 723 | Extra regulation sequence 1 heat I-time |  | 1 | 1800 | s | 70
243 | 726 | Extra regulation sequence 1 cool P-band |  | 1.00 | 10.00 | K | 6
244 | 729 | Extra regulation sequence 1 cool I-time |  | 1 | 1800 | s | 60
245 | 732
246 | 735
247 | 738 | Extra regulation 1 periodic operation interval |  | 0 | 168 | h | 24
248 | 741 | Extra regulation 1 periodic operation time |  | 0 | 60 | min | 3
249 | 744
250 | 747
251 | 750
252 | 753 | Extra regulation 1 temperature protection temperature |  | -50.00 | 100.00 | °C | 0.00
253 | 756 | Extra regulation 1 temperature protection alarm delay |  | 0 | 9999 | min | 5
254 | 759
255 | 762
256 | 765
257 | 768
258 | 771 | Cool step 1 min supply air flow limit |  | 0 | Vp5,259 | l/s |  | 1.16
259 | 774 | Cool step 2 min supply air flow limit |  | Vp5,258 | Vp5,260 | l/s |  | 1.16
260 | 777 | Cool step 3 min supply air flow limit |  | Vp5,259 | Vp2,57 | l/s |  | 1.16
261 | 780
262 | 783 | Cool SA neutral zone |  | 0.50 | 10.00 | K | 0.50
263 | 786 | Cool EA neutral zone |  | 0.50 | 10.00 | K | 0.50
264 | 789 | Cool outdoor temp limit 1 |  | 0.00 | 30.00 | °C | 15.00
265 | 792 | Cool outdoor temp limit 2 |  | 0.00 | 30.00 | °C | 18.00
266 | 795 | Cool outdoor temp limit 3 |  | 0.00 | 30.00 | °C | 20.00
267 | 798 | Cool 0-10V min supply air flow limit |  | 0 | Vp2,57 | l/s
268 | 801 | Cool 0-10V min extract air flow limit |  | 0 | Vp2,58 | l/s
269 | 804 | Cool restart time | Setting of cool restart time between start-start. | 0 | 15 | min | 5
270 | 807 | Cool step up delay time | Setting of on/off cooling and COOL DX time delay between steps. | 0 | 10 | min | 5
271 | 810 | Cool stand still time | Setting of on/off cooling and COOL DX time delay before stop-start | 0 | 20 | min | 5
272 | 813 | Cool P-band |  | 1.00 | 10.00 | K | 6
273 | 816 | Cool I-time |  | 1 | 1800 | s | 60
274 | 819
275 | 822
276 | 825
277 | 828 | Cool periodic operation interval |  | 0 | 168 | h | 24
278 | 831 | Cool periodic operation time |  | 0 | 60 | min | 3
279 | 834 | Cool step 1 min extract air flow limit |  | 0 | Vp5,280 | l/s |  | 1.16
280 | 837 | Cool step 2 min extract air flow limit |  | Vp5,279 | Vp5,281 | l/s |  | 1.16
281 | 840 | Cool step 3 min extract air flow limit |  | Vp5,280 | Vp2,58 | l/s |  | 1.16
282 | 843
283 | 846
Summer night cool/Intermittent night heat /Morning boost
284 | 849
285 | 852 | Summer night cool start time (hour) |  | 0 | 23 | h | 23
286 | 855 | Summer night cool start time (minute) |  | 0 | 59 | min | 0
287 | 858 | Summer night cool stop time (hour) |  | 0 | 23 | h | 23
288 | 861 | Summer night cool stop time (minute) |  | 0 | 59 | min | 0
289 | 864 | Summer night cool OA temp start limit |  | -5.00 | 15.00 | °C | 10.00
290 | 867 | Summer night cool EA temp start limit |  | 17.00 | 27.00 | °C | 22.00
291 | 870 | Summer night cool EA temp stop limit |  | 12.00 | 22.00 | °C | 16.00
292 | 873 | Summer night cool SA temp set point |  | 0.00 | 20.00 | °C | 10.00
293 | 876 | Summer night cool SA flow set point |  | Vp2,55 | Vp2,57 | l/s |  | 1.22
294 | 879 | Summer night cool EA flow set point |  | Vp2,56 | Vp2,58 | l/s |  | 1.22
295 | 882
296 | 885
297 | 888 | Intermittent night heat SA flow set point |  | Vp2,55 | Vp2,57 | l/s
298 | 891 | Intermittent night heat SA duct pressure set point |  | 20 | 750 | Pa | 100
299 | 894 | Intermittent night heat EA temp start limit |  | 5.00 | 300 | °C | 16.00
300 | 897 | Intermittent night heat EA temp stop limit |  | 299 | 25.00 | °C | 18.00
301 | 900 | Intermittent night heat SA temp set point |  | 5.00 | 50.00 | °C | 28.00
302 | 903
303 | 906 | Intermittent night heat EA flow set point |  | Vp2,56 | Vp2,58 | l/s |  | 1.12
304 | 909 | Intermittent night heat EA duct pressure set point |  | 20 | 750 | Pa |  | 1.12
305 | 912
306 | 915 | Morning boost start time (hour) |  | 0 | 23 | h | 0
307 | 918 | Morning boost start time (minute) |  | 0 | 59 | min | 0
308 | 921 | Morning boost air flow set point |  | Vp2,55 | Vp2,57 | l/s
309 | 924 | Morning boost duct pressure set point |  | 20 | 750 | Pa | 100
310 | 927
311 | 930 | Summer night cool SA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
312 | 933 | Summer night cool EA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
Cooling boost/heating boost
313 | 936
314 | 939 | Cooling boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
315 | 942 | Cooling boost comfort regulation speed |  | 0.01 | 25 | %/s | 4
316 | 945 | Cooling boost economy P-band |  | 1 | 10.00 | K
317 | 948 | Cooling boost economy I-time |  | 1 | 1800 | s
318 | 951
319 | 954
320 | 957
321 | 960 | Heating boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
322 | 963 | Heating boost comfort regulation speed |  | 0.01 | 25 | %/s | 4
323 | 966
324 | 969
325 | 972
326 | 975
327 | 978
328 | 981
329 | 984
330 | 987
Xzone ERS-1 reg.
331 | 990 | Xzone ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4
332 | 993 | Xzone ERS 1 diff | Supply air temp differental setting according to the diagram for ERS 1. | 1 | 7.00 | K | 2.00
333 | 996 | Xzone ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
334 | 999
335 | 1002
Xzone ERS-2 reg.
336 | 1005 | Xzone ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10 | Vp5,337 | °C | 15.00
337 | 1008 | Xzone ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | Vp5,336 | Vp5,338 | °C | 20.00
338 | 1011 | Xzone ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | Vp5,337 | Vp5,339 | °C | 22.00
339 | 1014 | Xzone ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | Vp5,338 | 40.00 | °C | 24.00
340 | 1017 | Xzone ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
341 | 1020 | Xzone ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
342 | 1023 | Xzone ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
343 | 1026 | Xzone ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
344 | 1029
345 | 1032
Xzone SA Reg.
346 | 1035 | Xzone SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
347 | 1038
348 | 1041
Xzone EA Reg.
349 | 1044 | Xzone EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
350 | 1047 | Xzone SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 20.00 | °C | 16.00
351 | 1050 | Xzone SA max temp set point | Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
352 | 1053 | Xzone EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
353 | 1056 | Xzone EA regultaion I-time |  | 1 | 1800 | s | 180
Xzone ORS Reg.
354 | 1059 | Xzone ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | Vp5,355 | °C | -20.00
355 | 1062 | Xzone ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | Vp5,354 | Vp5,356 | °C | -10.00
356 | 1065 | Xzone ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | Vp5,355 | Vp5,357 | °C | 10.00
357 | 1068 | Xzone ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | Vp5,356 | 50.00 | °C | 20.00
358 | 1071 | Xzone ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
359 | 1074 | Xzone ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
360 | 1077 | Xzone ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
361 | 1080 | Xzone ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
362 | 1083
363 | 1086
Xzone ORE Reg.
364 | 1089 | Xzone ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | Vp5,365 | °C | -20.00
365 | 1092 | Xzone ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | Vp5,364 | Vp5,366 | °C | -10.00
366 | 1095 | Xzone ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | Vp5,365 | Vp5,367 | °C | 10.00
367 | 1098 | Xzone ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | Vp5,366 | 50.00 | °C | 20.00
368 | 1101 | Xzone ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
369 | 1104 | Xzone ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
370 | 1107 | Xzone ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
371 | 1110 | Xzone ORE breakpoint Y4 |  | 10.00 | 40.00 | °C | 21.50
372 | 1113
373 | 1116
Xzone external sensors
374 | 1119
375 | 1122
376 | 1125
377 | 1128
378 | 1131
379 | 1134
380 | 1137 | Xzone external room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
381 | 1140 | Xzone external room temp from BMS alarm time |  | 0 | 9999 | min | 5
382 | 1143
383 | 1146
Xzone Heat/Cool
384 | 1149 | Xzone reheat P-band |  | 1.00 | 10.00 | K | 8.00
385 | 1152 | Xzone reheat I-time |  | 1 | 1800 | s | 70
386 | 1155
387 | 1158
388 | 1161 | Xzone reheat periodic operation interval |  | 0 | 168 | h | 24
389 | 1164 | Xzone reheat periodic operation time |  | 0 | 60 | min | 3
390 | 1167
391 | 1170
392 | 1173
393 | 1176
394 | 1179
395 | 1182
396 | 1185 | Xzone Cool SA neutral zone |  | 0.50 | 10.00 | K | 0.50
397 | 1188 | Xzone Cool EA neutral zone |  | 0.50 | 10.00 | K | 0.50
398 | 1191 | Xzone Cool P-band |  | 1.00 | 10.00 | K | 6.00
399 | 1194 | Xzone Cool I-time |  | 1 | 1800 | s | 60
400 | 1197
401 | 1200
402 | 1203
403 | 1206 | Xzone Cool periodic operation interval |  | 0 | 168 | h | 24
404 | 1209 | Xzone Cool periodic operation time |  | 0 | 60 | min | 3
405 | 1212
406 | 1215
407 | 1218
408 | 1221
409 | 1224
Pre-heat
410 | 1227
411 | 1230 | Pre-heat temperature set point |  | -40.00 | 40.00 | °C | 5.00
412 | 1233 | Pre-heat P-band |  | 1.00 | 10.00 | K | 8.00
413 | 1236 | Pre-heat I-time |  | 1 | 1800 | s | 70
414 | 1239
415 | 1242
416 | 1245 | Pre-heat periodic operation interval
417 | 1248 | Pre-heat periodic operation time
418 | 1251
419 | 1254
420 | 1257
421 | 1260
422 | 1263
ReCO2
423 | 1266
424 | 1269
425 | 1272
426 | 1275 | ReCO2-CO2 set point |  | 0.00 | 100.00 | % | 50.00
427 | 1278 | ReCO2 min. outdoor air |  | 0 | Vp2,57 | l/s
428 | 1281 | ReCO2 min. exhaust air |  | 0 | Vp2,58 | l/s
429 | 1284 | ReCO2-CO2 P-band |  | 1.00 | 100.00 | % | 50.00
430 | 1287 | ReCO2-CO2 I-time |  | 1 | 1800 | s | 60
431 | 1290 | ReCO2-CO2 air flow boost reg. P-band |  | 10.00 | 100.00 | % | 50.00
432 | 1293 | ReCO2-CO2 air flow boost reg. I-time |  | 1 | 1800 | s | 60
433 | 1296 | ReCO2 heat P-band |  | 1.00 | 10.00 | K | 7.00
434 | 1299 | ReCO2 heat I-time |  | 1 | 1800 | s | 70
435 | 1302 | ReCO2 cool P-band |  | 1.00 | 10.00 | K | 6.00
436 | 1305 | ReCO2 cool I-time |  | 1 | 1800 | s | 60
437 | 1308 | ReCO2-CO2 ppm set point |  | 0 | 10000 | ppm | 1000 | 1.28
438 | 1311 | ReCO2-CO2 ppm P-band |  | 100 | 10000 | ppm | 600 | 1.28
439 | 1314 | ReCO2-VOC ppm set point |  | 0 | 10000 | ppm | 1500 | 1.28
440 | 1317 | ReCO2-VOC ppm P-band |  | 100 | 10000 | ppm | 1000 | 1.28
Humidity/VOC
441 | 1320
442 | 1323
443 | 1326 | Humidifying on/off start level |  | 10.00 | Vp5,444 | %RH | 40.00
444 | 1329 | Humidifying on/off stop level |  | Vp5,443 | 95.00 | %RH | 45.00
445 | 1332
446 | 1335
447 | 1338
448 | 1341 | Humidifying 0-10V set point |  | 10.00 | 95.00 | %RH | 30.00
449 | 1344 | Humidifying 0-10V SA max set point |  | 10.00 | 95.00 | %RH | 80.00
450 | 1347 | Humidifying 0-10V SA P-band |  | 1.00 | 200.00 | %RH | 60.00
451 | 1350 | Humidifying 0-10V SA I-time |  | 1 | 1800 | s | 30
452 | 1353 | Humidifying 0-10V EA P-band |  | 1.00 | 200.00 | %RH | 60.00
453 | 1356 | Humidifying 0-10V EA I-time |  | 1 | 1800 | s | 180
454 | 1359
455 | 1362
456 | 1365
457 | 1368
458 | 1371 | Dehumidifying SA set point |  | 10.00 | 90.00 | %RH | 50.00
459 | 1374
460 | 1377 | Dehumidifying EA set point |  | 10.00 | 90.00 | %RH | 50.00 | 1.18
461 | 1380
462 | 1383
463 | 1386
464 | 1389
465 | 1392
466 | 1395
467 | 1398
468 | 1401
COOL DX
469 | 1404
470 | 1407 | COOL DX Low pressure stop limit |  | 1.00 | 10.00 | Bar | 3.00
471 | 1410 | COOL DX High pressure stop limit |  | 25.00 | 40.00 | Bar | 39.00
472 | 1413 | COOL DX Restart time | Time setting between start - start | 5 | 15 | min | 5
473 | 1416
474 | 1419
475 | 1422
476 | 1425
477 | 1428
478 | 1431
479 | 1434
480 | 1437
SMART Link
481 | 1440
482 | 1443 | SMART Link WB Heat temperature set point |  | Vp2,299 | Vp2,300 | °C | 40.0
483 | 1446 | SMART Link WB Heat temperature heat zone |  | 1.0 | 10.0 | K | 3.0
484 | 1449 | SMART Link WB Cool temperature set point |  | Vp2,301 | Vp2,302 | °C | 12.0
485 | 1452 | SMART Link WB Cool temperature heat zone |  | 1.0 | 10.0 | K | 2.0
486 | 1455
487 | 1458
488 | 1461
489 | 1464
490 | 1467
491 | 1470 | SMART Link WB Optimize valve upper limit |  | 5.0 | 90.0 | % | 80.0
492 | 1473 | SMART Link WB Optimize valve lower limit |  | 70.0 | 100.0 | % | 100.0
493 | 1476 | SMART Link WB Optimize time delay |  | 30 | 32000 | s | 60
494 | 1479 | SMART Link WB Optimize heat regulation speed |  | 0.001 | 1.000 | K/s | 0.005
495 | 1482 | SMART Link WB Optimize cool regulation speed |  | 0.001 | 1.000 | K/s | 0.010
496 | 1485
497 | 1488
498 | 1491
499 | 1494
500 | 1497
501 | 1500
502 | 1503
503 | 1506
504 | 1509
505 | 1512
506 | 1515
507 | 1518
508 | 1521
509 | 1524
510 | 1527 | SMART Link DX Amount of units |  | 0 | 4 |  | 1
511 | 1530
512 | 1533
513 | 1536
514 | 1539
515 | 1542
516 | 1545
517 | 1548
518 | 1551
519 | 1554 | SMART Link OA temp limit |  | -50.00 | 50.00 | °C | -30.00 | 1.12
520 | 1557
AYC
521 | 1560
522 | 1563
523 | 1566
524 | 1569 | AYC Heated water temp set point |  | 10.00 | 80.00 | °C | 30.00
525 | 1572
526 | 1575 | AYC Heated water OA temp for start of pump |  | -40.00 | 40.00 |  | 15.00
527 | 1578 | AYC Heated water OA temp for stop of pump |  | -40.00 | 40.00 |  | 18.00
528 | 1581
529 | 1584
530 | 1587
531 | 1590
532 | 1593 | AYC Heated water periodic operation interval |  | 0 | 168 | h | 24
533 | 1596 | AYC Heated water periodic operation time |  | 0 | 60 | min | 3
534 | 1599
535 | 1602
536 | 1605
537 | 1608 | AYC Heated water OA temp compensation X1 |  | -40.00 | Vp5,538 | °C | -20.00
538 | 1611 | AYC Heated water OA temp compensation X2 |  | Vp5,537 | Vp5,539 | °C | 0.00
539 | 1614 | AYC Heated water OA temp compensation X3 |  | Vp5,538 | Vp5,540 | °C | 5.00
540 | 1617 | AYC Heated water OA temp compensation X4 |  | Vp5,539 | 40.00 | °C | 15.00
541 | 1620 | AYC Heated water OA temp compensation Y1 |  | -40.00 | 40.00 | °C | 40.00
542 | 1623 | AYC Heated water OA temp compensation Y2 |  | -40.00 | 40.00 | °C | 30.00
543 | 1626 | AYC Heated water OA temp compensation Y3 |  | -40.00 | 40.00 | °C | 20.00
544 | 1629 | AYC Heated water OA temp compensation Y4 |  | -40.00 | 40.00 | °C | 15.00
545 | 1632
546 | 1635
547 | 1638
548 | 1641
549 | 1644 | AYC Heated water room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
550 | 1647 | AYC Heated water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
551 | 1650
552 | 1653
553 | 1656
554 | 1659 | AYC Heated water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
555 | 1662
556 | 1665 | AYC Heated water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
557 | 1668 | AYC Heated water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
558 | 1671 | AYC Heated water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
559 | 1674 | AYC Heated water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
560 | 1677
561 | 1680
562 | 1683
563 | 1686 | AYC Heated water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
564 | 1689 | AYC Heated water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
565 | 1692 | AYC Heated water night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
566 | 1695 | AYC Heated water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
567 | 1698
568 | 1701
569 | 1704 | AYC Heated water P-band |  | 1.00 | 40..00 | K | 15.00
570 | 1707 | AYC Heated water I-time |  | 1 | 600 | s | 60
571 | 1710
572 | 1713 | AYC Chilled water temp set point |  | 10.00 | 80.00 | °C | 30.00
573 | 1716
574 | 1719
575 | 1722 | AYC Chilled water OA temp for start of pump |  | -40.00 | 40.00 |  | 15.00
576 | 1725 | AYC Chilled water OA temp for stop of pump |  | -40.00 | 40.00 |  | 18.00
577 | 1728
578 | 1731
579 | 1734
580 | 1737
581 | 1740 | AYC Chilled water periodic operation interval |  | 0 | 168 | h | 24
582 | 1743 | AYC Chilled water periodic operation time |  | 0 | 60 | min | 3
583 | 1746
584 | 1749
585 | 1752
586 | 1755 | AYC Chilled water OA temp compensation X1 |  | -40.00 | Vp5,587 | °C | -20.00
587 | 1758 | AYC Chilled water OA temp compensation X2 |  | Vp5,586 | Vp5,588 | °C | 0.00
588 | 1761 | AYC Chilled water OA temp compensation X3 |  | Vp5,587 | Vp5,589 | °C | 5.00
589 | 1764 | AYC Chilled water OA temp compensation X4 |  | Vp5,588 | 40.00 | °C | 15.00
590 | 1767 | AYC Chilled water OA temp compensation Y1 |  | -40.00 | 40.00 | °C | 40.00
591 | 1770 | AYC Chilled water OA temp compensation Y2 |  | -40.00 | 40.00 | °C | 30.00
592 | 1773 | AYC Chilled water OA temp compensation Y3 |  | -40.00 | 40.00 | °C | 20.00
593 | 1776 | AYC Chilled water OA temp compensation Y4 |  | -40.00 | 40.00 | °C | 15.00
594 | 1779
595 | 1782
596 | 1785
597 | 1788
598 | 1791 | AYC Chilledwater room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
599 | 1794 | AYC Chilled water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
600 | 1797
601 | 1800
602 | 1803
603 | 1806 | AYC Chilled water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
604 | 1809
605 | 1812 | AYC Chilled water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
606 | 1815 | AYC Chilled water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
607 | 1818 | AYC Chilled water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
608 | 1821 | AYC Chilled water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
609 | 1824
610 | 1827
611 | 1830
612 | 1833 | AYC Chilled water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
613 | 1836 | AYC Chilled water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
614 | 1839 | AYC Chilledwater night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
615 | 1842 | AYC Chilled water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
616 | 1845
617 | 1848
618 | 1851
619 | 1854 | AYC Chilled water dew point compensation neutral zone |  | 0 | 5.00 | K | 2.00
620 | 1857 | AYC Chilled water dew point compensation regulation speed | Percent air flow boost of each increased chilled water set point. | 0 | 30.00 | %/K | 10.00
621 | 1860
622 | 1863
623 | 1866 | AYC Chilled water P-band |  | 1.00 | 40..00 | K | 15.00
624 | 1869 | AYC Chilled water I-time |  | 1 | 600 | s | 60
625 | 1872
626 | 1875
627 | 1878
628 | 1881
629 | 1884
630 | 1887
631 | 1890
632 | 1893
633 | 1896
634 | 1899
635 | 1902
636 | 1905
Optimize
637 | 1908
638 | 1911 | Optimize SA pressure set point |  | 20.0 | 750.0 | Pa | 0
639 | 1914 | Optimize EA pressure set point |  | 20.0 | 750.0 | Pa | 0
640 | 1917
641 | 1920
642 | 1923
643 | 1926
644 | 1929
645 | 1932
646 | 1935
647 | 1938
648 | 1941
649 | 1944
650 | 1947
651 | 1950
652 | 1953
653 | 1956
654 | 1959
MIRU Control
655 | 1962
656 | 1965
657 | 1968
658 | 1971
659 | 1974
660 | 1977
661 | 1980
662 | 1983
663 | 1986
664 | 1989
665 | 1992
666 | 1995
667 | 1998
668 | 2001
669 | 2004
670 | 2007
671 | 2010
672 | 2013 | MIRU Control 1 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
673 | 2016 | MIRU Control 1 High speed duct pressure set point |  | 0 | 750 | Pa | 200
674 | 2019 | MIRU Control 1 Low speed air flow set point |  | Vp2,400 | Vp2,401 | l/s
675 | 2022 | MIRU Control 1 High speed air flow set point |  | Vp2,400 | Vp2,401 | l/s
676 | 2025 | MIRU Control 1 offset factor for slave controlled air flow | Offset factor | 2.00 | 20.00 | % | 10.00 | 2.42
677 | 2028 | MIRU Control 1 fixed flow offset for slave controlled SA flow |  | 0 | Vp2,401 | l/s |  | 2.42
678 | 2031
679 | 2034
680 | 2037 | MIRU Control 2 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
681 | 2040 | MIRU Control 2 High speed duct pressure set point |  | 0 | 750 | Pa | 200
682 | 2043 | MIRU Control 2 Low speed air flow set point |  | Vp2,417 | Vp2,418 | l/s
683 | 2046 | MIRU Control 2 High speed air flow set point |  | Vp2,417 | Vp2,418 | l/s
684 | 2049 | MIRU Control 2 offset factor for slave controlled air flow | Offset factor | 2.00 | 20.00 | % | 10.00 | 2.42
685 | 2052 | MIRU Control 2 fixed flow offset for slave controlled SA flow |  | 0 | Vp2,418 | l/s |  | 2.42
686 | 2055
687 | 2058
688 | 2061 | MIRU Control 3 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
689 | 2064 | MIRU Control 3 High speed duct pressure set point |  | 0 | 750 | Pa | 200
690 | 2067 | MIRU Control 3 Low speed air flow set point |  | Vp2,434 | Vp2,435 | l/s
691 | 2070 | MIRU Control 3 High speed air flow set point |  | Vp2,434 | Vp2,435 | l/s
692 | 2073 | MIRU Control 3 offset factor for slave controlled air flow | Offset factor | 2.00 | 20.00 | % | 10.00 | 2.42
693 | 2076 | MIRU Control 3 fixed flow offset for slave controlled SA flow |  | 0 | Vp2,435 | l/s |  | 2.42
694 | 2079
695 | 2082
696 | 2085 | MIRU Control 4 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
697 | 2088 | MIRU Control 4 High speed duct pressure set point |  | 0 | 750 | Pa | 200
698 | 2091 | MIRU Control 4 Low speed air flow set point |  | Vp2,451 | Vp2,452 | l/s
699 | 2094 | MIRU Control 4 High speed air flow set point |  | Vp2,451 | Vp2,452 | l/s
700 | 2097
701 | 2100
702 | 2103
703 | 2106
704 | 2109 | MIRU Control 5 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
705 | 2112 | MIRU Control 5 High speed duct pressure set point |  | 0 | 750 | Pa | 200
706 | 2115 | MIRU Control 5 Low speed air flow set point |  | Vp2,468 | Vp2,469 | l/s
707 | 2118 | MIRU Control 5 High speed air flow set point |  | Vp2,468 | Vp2,469 | l/s
708 | 2121
709 | 2124
710 | 2127
711 | 2130
712 | 2133 | MIRU Control 6 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
713 | 2136 | MIRU Control 6 High speed duct pressure set point |  | 0 | 750 | Pa | 200
714 | 2139 | MIRU Control 6 Low speed air flow set point |  | Vp2,485 | Vp2,486 | l/s
715 | 2142 | MIRU Control 6 High speed air flow set point |  | Vp2,485 | Vp2,486 | l/s
716 | 2145
717 | 2148
718 | 2151
719 | 2154
720 | 2157 | MIRU Control 7 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
721 | 2160 | MIRU Control 7 High speed duct pressure set point |  | 0 | 750 | Pa | 200
722 | 2163 | MIRU Control 7 Low speed air flow set point |  | Vp2,502 | Vp2,503 | l/s
723 | 2166 | MIRU Control 7 High speed air flow set point |  | Vp2,502 | Vp2,503 | l/s
724 | 2169
725 | 2172
726 | 2175
727 | 2178
728 | 2181 | MIRU Control 8 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
729 | 2184 | MIRU Control 8 High speed duct pressure set point |  | 0 | 750 | Pa | 200
730 | 2187 | MIRU Control 8 Low speed air flow set point |  | Vp2,519 | Vp2,520 | l/s
731 | 2190 | MIRU Control 8 High speed air flow set point |  | Vp2,519 | Vp2,520 | l/s
732 | 2193
733 | 2196
734 | 2199
735 | 2202
736 | 2205 | MIRU Control 9 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
737 | 2208 | MIRU Control 9 High speed duct pressure set point |  | 0 | 750 | Pa | 200
738 | 2211 | MIRU Control 9 Low speed air flow set point |  | Vp2,536 | Vp2,537 | l/s
739 | 2214 | MIRU Control 9 High speed air flow set point |  | Vp2,536 | Vp2,537 | l/s
740 | 2217
741 | 2220
742 | 2223
743 | 2226
744 | 2229 | MIRU Control 10 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
745 | 2232 | MIRU Control 10 High speed duct pressure set point |  | 0 | 750 | Pa | 200
746 | 2235 | MIRU Control 10 Low speed air flow set point |  | Vp2,553 | Vp2,554 | l/s
747 | 2238 | MIRU Control 10 High speed air flow set point |  | Vp2,553 | Vp2,554 | l/s
748 | 2241
Efficiency measurement
752 | 2253 | Delta temperature alarm limit |  | 3.00 | 20.00 | K | 6.00 | 1.23
753 | 2256 | Efficiency alarm limit |  | 10.00 | 70.00 | % | 50.00 | 1.23
Neutral zone
754 | 2259 | Extra regulation sequence 1 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
755 | 2262 | Extra regulation sequence 2 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
756 | 2265 | ReCO2 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
757 | 2268 | H/C heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
758 | 2271 | Re-heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
759 | 2274 | Extra regulation sequence 1 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
760 | 2277 | Extra regulation sequence 2 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
761 | 2280 | ReCO2 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
762 | 2283 | H/C cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
763 | 2286 | Cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
764 | 2289 | Cooling boost neutral zone |  | 0 | 10.00 | K | 0 | 1.32
765 | 2292
766 | 2295
767 | 2298
768 | 2301
769 | 2304
BMS I/O-modules
800 | 2397 | External operation I/O-module A, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
801 | 2400 | External operation I/O-module B, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
802 | 2403 | External operation I/O-module C, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
Reserved
818 | 2451 | Extra regulation sequence 2 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00 | 1.13
819 | 2454 | Extra regulation sequence 2 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00 | 1.13
820 | 2457 | Extra regulation sequence 2 heat P-band |  | 1.00 | 10.00 | K | 8 | 1.13
821 | 2460 | Extra regulation sequence 2 heat I-time |  | 1 | 1800 | s | 70 | 1.13
822 | 2463 | Extra regulation sequence 2 cool P-band |  | 1.00 | 10.00 | K | 6 | 1.13
823 | 2466 | Extra regulation sequence 2 cool I-time |  | 1 | 1800 | s | 60 | 1.13
824 | 2469
825 | 2472
826 | 2475 | Extra regulation 2 periodic operation interval |  | 0 | 168 | h | 24 | 1.13
827 | 2478 | Extra regulation 2 periodic operation time |  | 0 | 60 | min | 3 | 1.13
828 | 2481
829 | 2484
830 | 2487 | Seasonal controlled supply air |  | 0.00 | 40.00 | C | 21.00 | 1.28
831 | 2490 | Seasonal controlled extract air/room temp |  | 0.00 | 40.00 | C | 21.00 | 1.28
832 | 2493 | Seasonal controlled supply air min temp |  | 0.00 | 30.00 | C | 16.00 | 1.28
833 | 2496 | Seasonal controlled supply air max temp |  | 8.00 | 50.00 | C | 28.00 | 1.28
834 | 2499
H/C
852 | 2553 | H/C outdoor temperature limit heating |  | -50.00 | 50.00 | °C | -20.00 | 1.23
853 | 2556 | H/C outdoor temperature limit cooling |  | 0.00 | 50.00 | °C | 15.00 | 1.23
854 | 2559 | H/C air flow limit supply air |  | 0 | Vp2,57 | l/s |  | 1.23
855 | 2562 | H/C air flow limit extract air |  | 0 | Vp2,58 | l/s |  | 1.23
Humidifying
891 | 2670 | Humidifying start time 1 (hour) |  | 0 | 23 | h | 0 | 2.37
892 | 2673 | Humidifying start time 1 (minute) |  | 0 | 59 | min | 0 | 2.37
893 | 2676 | Humidifying stop time 1 (hour) |  | 0 | 23 | h | 0 | 2.37
894 | 2679 | Humidifying stop time 1 (minute) |  | 0 | 59 | min | 0 | 2.37
895 | 2682
896 | 2685 | Humidifying start time 2 (hour) |  | 0 | 23 | h | 0 | 2.37
897 | 2688 | Humidifying start time 2 (minute) |  | 0 | 59 | min | 0 | 2.37
898 | 2691 | Humidifying stop time 2 (hour) |  | 0 | 23 | h | 0 | 2.37
899 | 2694 | Humidifying stop time 2 (minute) |  | 0 | 59 | min | 0 | 2.37
900 | 2697
901 | 2700 | Humidifying start time 3 (hour) |  | 0 | 23 | h | 0 | 2.37
902 | 2703 | Humidifying start time 3 (minute) |  | 0 | 59 | min | 0 | 2.37
903 | 2706 | Humidifying stop time 3 (hour) |  | 0 | 23 | h | 0 | 2.37
904 | 2709 | Humidifying stop time 3 (minute) |  | 0 | 59 | min | 0 | 2.37
905 | 2712
906 | 2715 | Humidifying start time 4 (hour) |  | 0 | 23 | h | 0 | 2.37
907 | 2718 | Humidifying start time 4 (minute) |  | 0 | 59 | min | 0 | 2.37
908 | 2721 | Humidifying stop time 4 (hour) |  | 0 | 23 | h | 0 | 2.37
909 | 2724 | Humidifying stop time 4 (minute) |  | 0 | 59 | min | 0 | 2.37
910 | 2727 | Humidifying start time | Humidifying time channel start level | 10.00 | Vp,911 | %RH | 50.00 | 2.37
911 | 2730 | Humidifying stop time | Humidifying time channel stop level | Vp5,910 | 95.00 | %RH | 55.00 | 2.37
912 | 2733 | Humidifying time | Humidifying time channel set point | 10.00 | 95.00 | %RH | 40.00 | 2.37
913 | 2736
914 | 2739
915 | 2742
Time schedule
916 | 2745 | Year | Setting for the unit's internal clock | 2000 | 2099 |  | 2000
917 | 2748
918 | 2751
919 | 2754
920 | 2757
921 | 2760
922 | 2763
923 | 2766
924 | 2769
925 | 2772
926 | 2775
927 | 2778
928 | 2781
929 | 2784
930 | 2787
931 | 2790
932 | 2793
933 | 2796
934 | 2799 | Effective period, Start year | 0=Unspecified | 2000 | 2099 |  | 2000
935 | 2802
936 | 2805
937 | 2808
938 | 2811 | Effective period, Stop year | 0=Unspecified | 2000 | 2099 |  | 2000
939 | 2814
940 | 2817
941 | 2820
942 | 2823
943 | 2826
944 | 2829
945 | 2832
946 | 2835
947 | 2838
948 | 2841
949 | 2844
950 | 2847
951 | 2850
952 | 2853
953 | 2856
954 | 2859
955 | 2862
956 | 2865
957 | 2868
958 | 2871
959 | 2874
960 | 2877
961 | 2880
962 | 2883
963 | 2886
964 | 2889
965 | 2892
966 | 2895
967 | 2898
968 | 2901
969 | 2904
970 | 2907
971 | 2910
972 | 2913
973 | 2916
974 | 2919
975 | 2922
976 | 2925
977 | 2928
978 | 2931
979 | 2934
980 | 2937
981 | 2940
982 | 2943
983 | 2946
984 | 2949
985 | 2952
986 | 2955
987 | 2958
988 | 2961
989 | 2964
990 | 2967
991 | 2970
992 | 2973
993 | 2976
994 | 2979
995 | 2982
996 | 2985
997 | 2988
998 | 2991
999 | 2994
1000 | 2997
1001 | 3000
1002 | 3003
1003 | 3006
1004 | 3009
1005 | 3012
1006 | 3015
1007 | 3018
1008 | 3021
1009 | 3024
1010 | 3027
1011 | 3030
1012 | 3033
1013 | 3036
1014 | 3039
1015 | 3042
1016 | 3045
1017 | 3048
1018 | 3051
1019 | 3054
1020 | 3057
1021 | 3060
1022 | 3063
1023 | 3066
1024 | 3069
1025 | 3072
1026 | 3075
1027 | 3078
1028 | 3081
1029 | 3084
1030 | 3087
1031 | 3090
1032 | 3093
1033 | 3096
1034 | 3099
1035 | 3102
1036 | 3105
1037 | 3108
1038 | 3111
1039 | 3114
1040 | 3117
1041 | 3120
1042 | 3123
1043 | 3126
1044 | 3129
1045 | 3132
1046 | 3135
1047 | 3138
1048 | 3141
1049 | 3144
1050 | 3147
1051 | 3150
1052 | 3153
1053 | 3156
1054 | 3159
1055 | 3162
1056 | 3165
1057 | 3168
1058 | 3171
1059 | 3174
1060 | 3177
1061 | 3180
1062 | 3183
1063 | 3186
1064 | 3189
1065 | 3192
1066 | 3195
1067 | 3198
1068 | 3201
1069 | 3204 | Exception schedule 1, start year | 0=Unspecified | 2000 | 2099 |  | 2000
1070 | 3207
1071 | 3210
1072 | 3213
1073 | 3216 | Exception schedule 1, stop year | 0=Unspecified | 2000 | 2099 |  | 2000
1074 | 3219
1075 | 3222
1076 | 3225
1077 | 3228
1078 | 3231
1079 | 3234 | Exception schedule 2, start year | 0=Unspecified | 2000 | 2099 |  | 2000
1080 | 3237
1081 | 3240
1082 | 3243
1083 | 3246 | Exception schedule 2, stop year | 0=Unspecified | 2000 | 2099 |  | 2000
1084 | 3249
1085 | 3252
1086 | 3255
1087 | 3258
1088 | 3261
1089 | 3264
1090 | 3267
1091 | 3270
1092 | 3273
1093 | 3276
1094 | 3279
1095 | 3282
1096 | 3285
1097 | 3288
1098 | 3291 | Calendar 1, Start year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
1099 | 3294 | Calendar 1, Start year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
1100 | 3297 | Calendar 1, Start year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
1101 | 3300 | Calendar 1, Start year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
1102 | 3303 | Calendar 1, Start year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
1103 | 3306 | Calendar 1, Start year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
1104 | 3309 | Calendar 1, Start year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
1105 | 3312 | Calendar 1, Start year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
1106 | 3315 | Calendar 1, Start year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
1107 | 3318 | Calendar 1, Start year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
1108 | 3321
1109 | 3324
1110 | 3327
1111 | 3330
1112 | 3333
1113 | 3336
1114 | 3339
1115 | 3342
1116 | 3345
1117 | 3348
1118 | 3351
1119 | 3354
1120 | 3357
1121 | 3360
1122 | 3363
1123 | 3366
1124 | 3369
1125 | 3372
1126 | 3375
1127 | 3378
1128 | 3381
1129 | 3384
1130 | 3387
1131 | 3390
1132 | 3393
1133 | 3396
1134 | 3399
1135 | 3402
1136 | 3405
1137 | 3408
1138 | 3411 | Calendar 1, Stop year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
1139 | 3414 | Calendar 1, Stop year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
1140 | 3417 | Calendar 1, Stop year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
1141 | 3420 | Calendar 1, Stop year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
1142 | 3423 | Calendar 1, Stop year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
1143 | 3426 | Calendar 1, Stop year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
1144 | 3429 | Calendar 1, Stop year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
1145 | 3432 | Calendar 1, Stop year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
1146 | 3435 | Calendar 1, Stop year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
1147 | 3438 | Calendar 1, Stop year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
1148 | 3441
1149 | 3444
1150 | 3447
1151 | 3450
1152 | 3453
1153 | 3456
1154 | 3459
1155 | 3462
1156 | 3465
1157 | 3468
1158 | 3471
1159 | 3474
1160 | 3477
1161 | 3480
1162 | 3483
1163 | 3486
1164 | 3489
1165 | 3492
1166 | 3495
1167 | 3498
1168 | 3501
1169 | 3504
1170 | 3507
1171 | 3510
1172 | 3513
1173 | 3516
1174 | 3519
1175 | 3522
1176 | 3525
1177 | 3528
1178 | 3531
1179 | 3534
1180 | 3537
1181 | 3540
1182 | 3543
1183 | 3546
1184 | 3549
1185 | 3552
1186 | 3555
1187 | 3558
1188 | 3561 | Calendar 2, Start year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
1189 | 3564 | Calendar 2, Start year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
1190 | 3567 | Calendar 2, Start year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
1191 | 3570 | Calendar 2, Start year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
1192 | 3573 | Calendar 2, Start year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
1193 | 3576 | Calendar 2, Start year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
1194 | 3579 | Calendar 2, Start year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
1195 | 3582 | Calendar 2, Start year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
1196 | 3585 | Calendar 2, Start year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
1197 | 3588 | Calendar 2, Start year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
1198 | 3591
1199 | 3594
1200 | 3597
1201 | 3600
1202 | 3603
1203 | 3606
1204 | 3609
1205 | 3612
1206 | 3615
1207 | 3618
1208 | 3621
1209 | 3624
1210 | 3627
1211 | 3630
1212 | 3633
1213 | 3636
1214 | 3639
1215 | 3642
1216 | 3645
1217 | 3648
1218 | 3651
1219 | 3654
1220 | 3657
1221 | 3660
1222 | 3663
1223 | 3666
1224 | 3669
1225 | 3672
1226 | 3675
1227 | 3678
1228 | 3681 | Calendar 2, Stop year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
1229 | 3684 | Calendar 2, Stop year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
1230 | 3687 | Calendar 2, Stop year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
1231 | 3690 | Calendar 2, Stop year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
1232 | 3693 | Calendar 2, Stop year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
1233 | 3696 | Calendar 2, Stop year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
1234 | 3699 | Calendar 2, Stop year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
1235 | 3702 | Calendar 2, Stop year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
1236 | 3705 | Calendar 2, Stop year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
1237 | 3708 | Calendar 2, Stop year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
1238 | 3711

## Vpac 6 (RW)
GOLD_E_F_EXOline_250905
Index var. Vpac 6 (R/W)
Index | Cell nbr | Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
1 | 0 | SA Fan regulation mode | Setting of regulation type for the supply air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan | 0 | 3 |  | 0
2 | 1 | EA Fan regulation mode | Setting of regulation type for the extract air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan | 0 | 3 |  | 0
Fans OA temp compensation
53 | 52 | Outdoor temp compensation function | 0=Inactive, 1=Active at low speed, 2=Active at high speed, 3=Active at low and high speed. | 0 | 3 |  | 0
54 | 53
55 | 54
56 | 55
57 | 56
58 | 57
59 | 58
60 | 59
61 | 60
62 | 61
63 | 62
64 | 63
65 | 64
66 | 65
67 | 66
68 | 67
69 | 68
70 | 69
71 | 70
72 | 71
73 | 72
74 | 73
75 | 74
76 | 75
77 | 76
Fans down regulation
78 | 77 | Down regulation function | 0=Inactive, 1=SA, 2=SA and EA | 0 | 2 |  | 1
79 | 78
80 | 79
81 | 80
82 | 81
83 | 82
Fans in operation at active fire alarm
84 | 83 | Fans in operation at fire alarm 1 function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
85 | 84
86 | 85
87 | 86 | Fans in operation at fire alarm 2 function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
88 | 87
89 | 88
90 | 89 | Fans in operation at internal fire alarm function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
91 | 90
92 | 91
93 | 92
94 | 93
Filters
95 | 94 | Pre-filter function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
96 | 95 | Pre-filter calibration | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
97 | 96
98 | 97
99 | 98
100 | 99
101 | 100 | AHU filter function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
102 | 101 | AHU filter calibration | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
103 | 102
104 | 103
105 | 104
106 | 105
107 | 106 | SA end filter function | 0=Inactive, 1=SA | 0 | 1
108 | 107 | SA end filter calibration | 0=Inactive, 1=SA | 0 | 1
109 | 108
110 | 109
Seasonal controlled temperature regulation
111 | 110 | Seasonal controlled temperature regulation | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 1.23
112 | 111 | Seasonal controlled temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 4 | 1.23
113 | 112
114 | 113
AHU Temperature regulation
115 | 114 | Temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 3
116 | 115
AHU external sensors
162 | 161
163 | 162
164 | 163
165 | 164
166 | 165 | External room sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
167 | 166
168 | 167
169 | 168
170 | 169
171 | 170
172 | 171
173 | 172
174 | 173
175 | 174
176 | 175 | External OA sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
177 | 176
AHU Heat exchange
188 | 187 | RHX sorption rotor function | Setting for activating the sorption rotor control function for the rotary heat exchanger. 0=inactive, 1=sorption max speed at cool recovery, 2=always sorption max speed. | 0 | 2 |  | 0 | 2.36
189 | 188 | Rotor type | 0=RECOnomic, 1=STE, 2=MPE, 3=MTE | 0 | 3 |  | 0 | 2.36
AHU Heat/Cool
226 | 225
227 | 226
228 | 227
229 | 228
230 | 229
231 | 230
232 | 231
233 | 232
234 | 233
235 | 234
236 | 235 | Extra regulation 1 combi coil output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.37
237 | 236 | Extra regulation sequence 1 function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
238 | 237 | Extra regulation sequence 1 output function | 0=0-10V, 1=10-0V | 0 | 1 |  | 0
239 | 238
240 | 239
241 | 240
242 | 241
243 | 242
244 | 243
245 | 244
246 | 245
247 | 246
248 | 247
249 | 248 | Extra regulation 1 combi coil external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 1.26
250 | 249 | Extra regulation 1 combi coil external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 1.26
251 | 250 | Extra regulation 1 temperature protection function |  | 0 | 1 |  | 0
252 | 251
253 | 252
254 | 253 | Season heat function | 0=Inactive, 1=Extra regulation sequence at closed input, 2=Extra regulation sequence at open input, 3=Manual mode. | 0 | 3 |  | 0
255 | 254 | Season heat manual setting | 0=Re-heat, 1=Extra regulation sequence | 0 | 1 |  | 0
256 | 255
257 | 256
258 | 257
259 | 258
260 | 259
261 | 260 | Cool on/off regulation function | 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
262 | 261
Summer night cool
284 | 283 | Summer night cool function | 0=Inactive, 1=Internal, 2=External(BMS) | 0 | 2 |  | 0 | 2.46
295 | 294 | Summer night cool from communication | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.46
Cooling boost/heating boost
313 | 312 | Cooling boost function | 0=Inactive, 1=Comfort, 2=Economy, 3=Sequence, 4=Comfort and Economy, 5=Economy and Sequence | 0 | 5 |  | 0
314 | 313
315 | 314
316 | 315
317 | 316
318 | 317
319 | 318
320 | 319
321 | 320
322 | 321
323 | 322
324 | 323
325 | 324
326 | 325
327 | 326
328 | 327
Xzone temperature regulation
329 | 328 | Xzone temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 3
330 | 329
Xzone external sensors
378 | 377 | Xzone external room sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
379 | 378
380 | 379
381 | 380
382 | 381
383 | 382
Xzone Heat/Cool
384 | 383
385 | 384
386 | 385
387 | 386
388 | 387
389 | 388
390 | 389 | Xzone combi coil module A external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
391 | 390 | Xzone combi coil module A output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
392 | 391 | Xzone combi coil module A external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.43
393 | 392
394 | 393
395 | 394 | Xzone Cool on/off regulation function | 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
396 | 395
397 | 396
398 | 397
399 | 398
400 | 399
401 | 400
402 | 401
403 | 402
404 | 403
405 | 404 | Xzone combi coil module B external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
406 | 405 | Xzone combi coil module B output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
407 | 406 | Xzone combi coil module B external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.43
408 | 407
409 | 408
410 | 409
411 | 410
412 | 411
413 | 412
414 | 413
415 | 414
416 | 415
417 | 416
418 | 417
419 | 418
420 | 419
421 | 420
422 | 421
ReCO2
423 | 422 | ReCO2-CO2 function | 0=Inactive, 1=CO2, 2=CO2 and air flow boost | 0 | 2 |  | 0
424 | 423 | ReCO2 temperature regulation sequence function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
425 | 424
426 | 425
427 | 426
428 | 427
429 | 428
430 | 429
431 | 430
432 | 431
433 | 432
434 | 433
435 | 434
436 | 435
437 | 436
438 | 437
439 | 438
440 | 439
Humidity/VOC
441 | 440 | Humidifying function | 0=Inactive, 1=on/off, 2=0-10V | 0 | 2 |  | 0
442 | 441 | Humidifying sensor | 0=SA, 1=EA | 0 | 1 |  | 0
443 | 442
444 | 443
445 | 444
446 | 445
447 | 446
448 | 447
449 | 448
450 | 449
451 | 450
452 | 451
453 | 452
454 | 453
455 | 454
456 | 455
457 | 456 | Dehumidifying function | 0=Inactive, 1=SA, 2=EA, 3=Room(2.42) | 0 | 3 |  | 1 | 1.12
458 | 457
459 | 458
460 | 459
461 | 460
462 | 461
463 | 462
464 | 463
465 | 464 | VOC sensor function | 0=Inactive, 1=Monitoring only, 2=Monitoring and regulation | 0 | 2 |  | 0 | 1.23
466 | 465
467 | 466
468 | 467
COOL DX
469 | 468 | COOL DX Function | 0=Inactive, 1=Economy, 2=Comfort, 3=Top | 0 | 3 |  | 0
470 | 469
471 | 470
472 | 471
Exhaust heat
473 | 472 | Constant exhaust air temperature function | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.43
474 | 473
475 | 474
476 | 475
477 | 476
478 | 477
479 | 478
480 | 479
SMART Link
481 | 480 | SMART Link Function | 0=Inactive, 1=Water based heat pump, 2=Water based chiller, 3=Water based reversible, 4=DX based heat pump, 5=DX based chiller, 6=DX based reversible, | 0 | 6 |  | 0
482 | 481
483 | 482
484 | 483
485 | 484
486 | 485
487 | 486
488 | 487
489 | 488
490 | 489
491 | 490
492 | 491
493 | 492
494 | 493
495 | 494
496 | 495
497 | 496
498 | 497
499 | 498
500 | 499
501 | 500
502 | 501
503 | 502
504 | 503
505 | 504 | AQUA Link Pump alarm function | 0=Inactive, 1=alarm at closed contact, 2=Alarm at open contact, 3=Alarm when in -and output are unequal (contactor function). | 0 | 3 |  | 0
506 | 505
507 | 506
508 | 507
509 | 508
510 | 509
511 | 510
512 | 511
513 | 512
514 | 513
515 | 514
516 | 515
517 | 516
518 | 517
519 | 518
520 | 519
AYC
521 | 520 | AYC Function | 0=Inactive, 1=Chilled water, 2=Heated water, 3=Chilled and heated water | 0 | 3 |  | 0
522 | 521
523 | 522
524 | 523
525 | 524
526 | 525
527 | 526
528 | 527 | AYC Heated water signal monitor function for pump | 0=Inactive, 1=Alarm at open contact, 2=Alarm at closed contact, 3=Contactor function | 0 | 3 |  | 0
529 | 528
530 | 529
531 | 530
532 | 531
533 | 532
534 | 533
535 | 534
536 | 535
537 | 536
538 | 537
539 | 538
540 | 539
541 | 540
542 | 541
543 | 542
544 | 543
545 | 544
546 | 545
547 | 546
548 | 547
549 | 548
550 | 549
551 | 550
552 | 551
553 | 552
554 | 553
555 | 554 | AYC Heated water night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
556 | 555
557 | 556
558 | 557
559 | 558
560 | 559
561 | 560
562 | 561 | AYC Heated water night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
563 | 562
564 | 563
565 | 564
566 | 565
567 | 566
568 | 567
569 | 568
570 | 569
571 | 570
572 | 571
573 | 572
574 | 573
575 | 574
576 | 575
577 | 576 | AYC Chilled water signal monitor function for pump | 0=Inactive, 1=Alarm at open contact, 2=Alarm at closed contact, 3=Contactor function | 0 | 3 |  | 0
578 | 577
579 | 578
580 | 579
581 | 580
582 | 581
583 | 582
584 | 583
585 | 584
586 | 585
587 | 586
588 | 587
589 | 588
590 | 589
591 | 590
592 | 591
593 | 592
594 | 593
595 | 594
596 | 595
597 | 596
598 | 597
599 | 598
600 | 599
601 | 600
602 | 601
603 | 602
604 | 603 | AYC Chilled water night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
605 | 604
606 | 605
607 | 606
608 | 607
609 | 608
610 | 609
611 | 610 | AYC Chilled water night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
612 | 611
613 | 612
614 | 613
615 | 614
616 | 615
617 | 616
618 | 617
619 | 618
620 | 619
621 | 620
622 | 621
623 | 622
624 | 623
625 | 624
626 | 625
627 | 626
628 | 627
629 | 628
630 | 629
631 | 630
632 | 631
633 | 632
634 | 633
635 | 634
636 | 635
637 | 636
638 | 637
639 | 638
640 | 639
641 | 640
642 | 641
643 | 642
644 | 643
645 | 644
646 | 645
647 | 646
648 | 647
649 | 648
650 | 649
651 | 650
652 | 651
653 | 652
654 | 653
MIRU Control
655 | 654
656 | 655
657 | 656
658 | 657
659 | 658
660 | 659 | MIRU Control 1 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
661 | 660 | MIRU Control 2 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
662 | 661 | MIRU Control 3 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
663 | 662 | MIRU Control 4 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
664 | 663 | MIRU Control 5 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
665 | 664 | MIRU Control 6 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
666 | 665 | MIRU Control 7 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
667 | 666 | MIRU Control 8 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
668 | 667 | MIRU Control 9 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
669 | 668 | MIRU Control 10 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
670 | 669
671 | 670 | MIRU Control 1 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
672 | 671
673 | 672
674 | 673
675 | 674
676 | 675
677 | 676
678 | 677
679 | 678 | MIRU Control 2 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
680 | 679
681 | 680
682 | 681
683 | 682
684 | 683
685 | 684
686 | 685
687 | 686 | MIRU Control 3 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
688 | 687
689 | 688
690 | 689
691 | 690
692 | 691
693 | 692
694 | 693
695 | 694 | MIRU Control 4 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
696 | 695
697 | 696
698 | 697
699 | 698
700 | 699
701 | 700
702 | 701
703 | 702 | MIRU Control 5 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
704 | 703
705 | 704
706 | 705
707 | 706
708 | 707
709 | 708
710 | 709
711 | 710 | MIRU Control 6 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
712 | 711
713 | 712
714 | 713
715 | 714
716 | 715
717 | 716
718 | 717
719 | 718 | MIRU Control 7 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
720 | 719
721 | 720
722 | 721
723 | 722
724 | 723
725 | 724
726 | 725
727 | 726 | MIRU Control 8 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
728 | 727
729 | 728
730 | 729
731 | 730
732 | 731
733 | 732
734 | 733
735 | 734 | MIRU Control 9 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
736 | 735
737 | 736
738 | 737
739 | 738
740 | 739
741 | 740
742 | 741
743 | 742 | MIRU Control 10 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
744 | 743
745 | 744
746 | 745
747 | 746
748 | 747
749 | 748
750 | 749
751 | 750
752 | 751
753 | 752
754 | 753
755 | 754
756 | 755
757 | 756
758 | 757
759 | 758
760 | 759
761 | 760
762 | 761
763 | 762
764 | 763
Neutral zone
765 | 764 | Heat neutral zone function | 0=Set point, 1=Start limit. | 0 | 1 |  | 0 | 1.32
766 | 765 | Cool neutral zone function | 0=Set point, 1=Start limit. | 0 | 1 |  | 0 | 1.32
767 | 766
768 | 767
769 | 768
770 | 769
771 | 770
772 | 771
773 | 772
774 | 773
Night temp compensation
775 | 774 | Night temp compensation function |  | 0 | 1 |  | 0 | 1.31
776 | 775 | Night temp compensation temp |  | -10.00 | 0 | K | -2.00 | 1.31
777 | 776 | Night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 1.31
778 | 777 | Night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0 | 1.31
779 | 778 | Night temp compensation start time 1 (minute) |  | 0 | 59 | min | 0 | 1.31
780 | 779 | Night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0 | 1.31
781 | 780 | Night temp compensation stop time 1 (minute) |  | 0 | 59 | min | 0 | 1.31
782 | 781 | Night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 1.31
783 | 782 | Night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0 | 1.31
784 | 783 | Night temp compensation start time 2 (minute) |  | 0 | 59 | min | 0 | 1.31
785 | 784 | Night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0 | 1.31
786 | 785 | Night temp compensation stop time 2 (minute) |  | 0 | 59 | min | 0 | 1.31
787 | 786
788 | 787
789 | 788
790 | 789
791 | 790
792 | 791
Operation level settings
793 | 792 | Communication operation level | 0=auto, 1=total stop, 2=low speed, 3=high speed, 4=normal stop, 5=extended normal stop. | 0 | 5 |  | 0
794 | 793
Reserved
816 | 815 | Extra regulation sequence 2 function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0 | 1.13
817 | 816 | Extra regulation sequence 2 output function | 0=0-10V, 1=10-0V | 0 | 1 |  | 0 | 1.13
818 | 817
819 | 818
820 | 819
821 | 820
822 | 821
823 | 822
824 | 823
825 | 824
826 | 825
827 | 826
828 | 827 | Extra regulation 2 combi coil external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 1.26
829 | 828 | Extra regulation 2 combi coil external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 1.26
830 | 829
831 | 830
832 | 831
833 | 832
834 | 833 | Extra regulation 2 combi coil output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.37
H/C
850 | 849 | H/C heat mode | 0=Standard, 1=Comfort | 0 | 1 |  | 0 | 1.23
851 | 850 | H/C cool mode | 0=Standard, 1=Comfort | 0 | 1 |  | 0 | 1.23
Humidifying
890 | 889 | Humidifying time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
891 | 890
892 | 891
893 | 892
894 | 893
895 | 894 | Humidifying time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
896 | 895
897 | 896
898 | 897
899 | 898
900 | 899 | Humidifying time 3 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
901 | 900
902 | 901
903 | 902
904 | 903
905 | 904 | Humidifying time 4 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
Time schedule
916 | 915
917 | 916 | Month | Setting for the unit's internal clock | 1 | 12 |  | 1
918 | 917 | Date | Setting for the unit's internal clock | 1 | 31 |  | 1
919 | 918 | Hour | Setting for the unit's internal clock | 0 | 23 |  | 0
920 | 919 | Minute | Setting for the unit's internal clock | 0 | 59 |  | 0
921 | 920 | Second | Setting for the unit's internal clock | 0 | 59 |  | 0
922 | 921
923 | 922
924 | 923
925 | 924
926 | 925
927 | 926
928 | 927
929 | 928
930 | 929
931 | 930
932 | 931 | Default action | 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5 |  | 2
933 | 932
934 | 933
935 | 934 | Effective period, Start month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
936 | 935 | Effective period, Start date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
937 | 936 | Effective period, Start week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
938 | 937
939 | 938 | Effective period, Stop month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
940 | 939 | Effective period, Stop date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
941 | 940 | Effective period, Stop week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
942 | 941 | Day schedule, Monday hour #1 |  | 0 | 23 | h | 0
943 | 942 | Day schedule, Monday hour #2 |  | 0 | 23 | h | 0
944 | 943 | Day schedule, Monday hour #3 |  | 0 | 23 | h | 0
945 | 944 | Day schedule, Monday hour #4 |  | 0 | 23 | h | 0
946 | 945 | Day schedule, Monday hour #5 |  | 0 | 23 | h | 0
947 | 946 | Day schedule, Monday hour #6 |  | 0 | 23 | h | 0
948 | 947 | Day schedule, Monday minute #1 |  | 0 | 59 | min | 0
949 | 948 | Day schedule, Monday minute #2 |  | 0 | 59 | min | 0
950 | 949 | Day schedule, Monday minute #3 |  | 0 | 59 | min | 0
951 | 950 | Day schedule, Monday minute #4 |  | 0 | 59 | min | 0
952 | 951 | Day schedule, Monday minute #5 |  | 0 | 59 | min | 0
953 | 952 | Day schedule, Monday minute #6 |  | 0 | 59 | min | 0
954 | 953 | Day schedule, Monday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
955 | 954 | Day schedule, Monday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
956 | 955 | Day schedule, Monday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
957 | 956 | Day schedule, Monday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
958 | 957 | Day schedule, Monday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
959 | 958 | Day schedule, Monday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
960 | 959 | Day schedule, Tuesday hour #1 |  | 0 | 23 | h | 0
961 | 960 | Day schedule, Tuesday hour #2 |  | 0 | 23 | h | 0
962 | 961 | Day schedule, Tuesday hour #3 |  | 0 | 23 | h | 0
963 | 962 | Day schedule, Tuesday hour #4 |  | 0 | 23 | h | 0
964 | 963 | Day schedule, Tuesday hour #5 |  | 0 | 23 | h | 0
965 | 964 | Day schedule, Tuesday hour #6 |  | 0 | 23 | h | 0
966 | 965 | Day schedule, Tuesday minute #1 |  | 0 | 59 | min | 0
967 | 966 | Day schedule, Tuesday minute #2 |  | 0 | 59 | min | 0
968 | 967 | Day schedule, Tuesday minute #3 |  | 0 | 59 | min | 0
969 | 968 | Day schedule, Tuesday minute #4 |  | 0 | 59 | min | 0
970 | 969 | Day schedule, Tuesday minute #5 |  | 0 | 59 | min | 0
971 | 970 | Day schedule, Tuesday minute #6 |  | 0 | 59 | min | 0
972 | 971 | Day schedule, Tuesday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
973 | 972 | Day schedule, Tuesday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
974 | 973 | Day schedule, Tuesday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
975 | 974 | Day schedule, Tuesday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
976 | 975 | Day schedule, Tuesday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
977 | 976 | Day schedule, Tuesday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
978 | 977 | Day schedule, Wednesday hour #1 |  | 0 | 23 | h | 0
979 | 978 | Day schedule, Wednesday hour #2 |  | 0 | 23 | h | 0
980 | 979 | Day schedule, Wednesday hour #3 |  | 0 | 23 | h | 0
981 | 980 | Day schedule, Wednesday hour #4 |  | 0 | 23 | h | 0
982 | 981 | Day schedule, Wednesday hour #5 |  | 0 | 23 | h | 0
983 | 982 | Day schedule, Wednesday hour #6 |  | 0 | 23 | h | 0
984 | 983 | Day schedule, Wednesday minute #1 |  | 0 | 59 | min | 0
985 | 984 | Day schedule, Wednesday minute #2 |  | 0 | 59 | min | 0
986 | 985 | Day schedule, Wednesday minute #3 |  | 0 | 59 | min | 0
987 | 986 | Day schedule, Wednesday minute #4 |  | 0 | 59 | min | 0
988 | 987 | Day schedule, Wednesday minute #5 |  | 0 | 59 | min | 0
989 | 988 | Day schedule, Wednesday minute #6 |  | 0 | 59 | min | 0
990 | 989 | Day schedule, Wednesday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
991 | 990 | Day schedule, Wednesday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
992 | 991 | Day schedule, Wednesday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
993 | 992 | Day schedule, Wednesday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
994 | 993 | Day schedule, Wednesday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
995 | 994 | Day schedule, Wednesday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
996 | 995 | Day schedule, Thursday hour #1 |  | 0 | 23 | h | 0
997 | 996 | Day schedule, Thursday hour #2 |  | 0 | 23 | h | 0
998 | 997 | Day schedule, Thursday hour #3 |  | 0 | 23 | h | 0
999 | 998 | Day schedule, Thursday hour #4 |  | 0 | 23 | h | 0
1000 | 999 | Day schedule, Thursday hour #5 |  | 0 | 23 | h | 0
1001 | 1000 | Day schedule, Thursday hour #6 |  | 0 | 23 | h | 0
1002 | 1001 | Day schedule, Thursday minute #1 |  | 0 | 59 | min | 0
1003 | 1002 | Day schedule, Thursday minute #2 |  | 0 | 59 | min | 0
1004 | 1003 | Day schedule, Thursday minute #3 |  | 0 | 59 | min | 0
1005 | 1004 | Day schedule, Thursday minute #4 |  | 0 | 59 | min | 0
1006 | 1005 | Day schedule, Thursday minute #5 |  | 0 | 59 | min | 0
1007 | 1006 | Day schedule, Thursday minute #6 |  | 0 | 59 | min | 0
1008 | 1007 | Day schedule, Thursday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1009 | 1008 | Day schedule, Thursday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1010 | 1009 | Day schedule, Thursday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1011 | 1010 | Day schedule, Thursday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1012 | 1011 | Day schedule, Thursday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1013 | 1012 | Day schedule, Thursday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1014 | 1013 | Day schedule, Friday hour #1 |  | 0 | 23 | h | 0
1015 | 1014 | Day schedule, Friday hour #2 |  | 0 | 23 | h | 0
1016 | 1015 | Day schedule, Friday hour #3 |  | 0 | 23 | h | 0
1017 | 1016 | Day schedule, Friday hour #4 |  | 0 | 23 | h | 0
1018 | 1017 | Day schedule, Friday hour #5 |  | 0 | 23 | h | 0
1019 | 1018 | Day schedule, Friday hour #6 |  | 0 | 23 | h | 0
1020 | 1019 | Day schedule, Friday minute #1 |  | 0 | 59 | min | 0
1021 | 1020 | Day schedule, Friday minute #2 |  | 0 | 59 | min | 0
1022 | 1021 | Day schedule, Friday minute #3 |  | 0 | 59 | min | 0
1023 | 1022 | Day schedule, Friday minute #4 |  | 0 | 59 | min | 0
1024 | 1023 | Day schedule, Friday minute #5 |  | 0 | 59 | min | 0
1025 | 1024 | Day schedule, Friday minute #6 |  | 0 | 59 | min | 0
1026 | 1025 | Day schedule, Friday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1027 | 1026 | Day schedule, Friday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1028 | 1027 | Day schedule, Friday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1029 | 1028 | Day schedule, Friday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1030 | 1029 | Day schedule, Friday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1031 | 1030 | Day schedule, Friday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1032 | 1031 | Day schedule, Saturday hour #1 |  | 0 | 23 | h | 0
1033 | 1032 | Day schedule, Saturday hour #2 |  | 0 | 23 | h | 0
1034 | 1033 | Day schedule, Saturday hour #3 |  | 0 | 23 | h | 0
1035 | 1034 | Day schedule, Saturday hour #4 |  | 0 | 23 | h | 0
1036 | 1035 | Day schedule, Saturday hour #5 |  | 0 | 23 | h | 0
1037 | 1036 | Day schedule, Saturday hour #6 |  | 0 | 23 | h | 0
1038 | 1037 | Day schedule, Saturday minute #1 |  | 0 | 59 | min | 0
1039 | 1038 | Day schedule, Saturday minute #2 |  | 0 | 59 | min | 0
1040 | 1039 | Day schedule, Saturday minute #3 |  | 0 | 59 | min | 0
1041 | 1040 | Day schedule, Saturday minute #4 |  | 0 | 59 | min | 0
1042 | 1041 | Day schedule, Saturday minute #5 |  | 0 | 59 | min | 0
1043 | 1042 | Day schedule, Saturday minute #6 |  | 0 | 59 | min | 0
1044 | 1043 | Day schedule, Saturday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1045 | 1044 | Day schedule, Saturday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1046 | 1045 | Day schedule, Saturday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1047 | 1046 | Day schedule, Saturday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1048 | 1047 | Day schedule, Saturday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1049 | 1048 | Day schedule, Saturday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1050 | 1049 | Day schedule, Sunday hour #1 |  | 0 | 23 | h | 0
1051 | 1050 | Day schedule, Sunday hour #2 |  | 0 | 23 | h | 0
1052 | 1051 | Day schedule, Sunday hour #3 |  | 0 | 23 | h | 0
1053 | 1052 | Day schedule, Sunday hour #4 |  | 0 | 23 | h | 0
1054 | 1053 | Day schedule, Sunday hour #5 |  | 0 | 23 | h | 0
1055 | 1054 | Day schedule, Sunday hour #6 |  | 0 | 23 | h | 0
1056 | 1055 | Day schedule, Sunday minute #1 |  | 0 | 59 | min | 0
1057 | 1056 | Day schedule, Sunday minute #2 |  | 0 | 59 | min | 0
1058 | 1057 | Day schedule, Sunday minute #3 |  | 0 | 59 | min | 0
1059 | 1058 | Day schedule, Sunday minute #4 |  | 0 | 59 | min | 0
1060 | 1059 | Day schedule, Sunday minute #5 |  | 0 | 59 | min | 0
1061 | 1060 | Day schedule, Sunday minute #6 |  | 0 | 59 | min | 0
1062 | 1061 | Day schedule, Sunday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1063 | 1062 | Day schedule, Sunday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1064 | 1063 | Day schedule, Sunday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1065 | 1064 | Day schedule, Sunday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1066 | 1065 | Day schedule, Sunday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1067 | 1066 | Day schedule, Sunday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
1068 | 1067 | Exception schedule 1, function | 0=Date setting valid (MaxStartDate = 34) 1=Date range setting valid (MaxStartDate = 34) 2=Weekday setting valid (MaxStartDate = 6) 3=Calendar-1 setting valid 4=Calendar-2 setting valid 5=Inactive | 0 | 5 |  | 3 | 1.11
1069 | 1068
1070 | 1069 | Exception schedule 1, start month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1071 | 1070 | Exception schedule 1, start date | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1072 | 1071 | Exception schedule 1, start week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1073 | 1072
1074 | 1073 | Exception schedule 1, stop month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1075 | 1074 | Exception schedule 1, stop date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1076 | 1075 | Exception schedule 1, stop week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1077 | 1076 | Exception schedule 1, priority | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has highest priority) | 1 | 16 |  | 0
1078 | 1077 | Exception schedule 2, function | 0=Date setting valid (MaxStartDate = 34) 1=Date range setting valid (MaxStartDate = 34) 2=Weekday setting valid (MaxStartDate = 6) 3=Calendar-1 setting valid 4=Calendar-2 setting valid 5=Inactive | 0 | 5 |  | 4 | 1.11
1079 | 1078
1080 | 1079 | Exception schedule 2, start month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1081 | 1080 | Exception schedule 2, start date | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1082 | 1081 | Exception schedule 2, start week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1083 | 1082
1084 | 1083 | Exception schedule 2, stop month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1085 | 1084 | Exception schedule 2, stop date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1086 | 1085 | Exception schedule 2, stop week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1087 | 1086 | Exception schedule 2, priority | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has highest priority) | 1 | 16 |  | 0
1088 | 1087 | Calendar 1, function #1 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1089 | 1088 | Calendar 1, function #2 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1090 | 1089 | Calendar 1, function #3 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1091 | 1090 | Calendar 1, function #4 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1092 | 1091 | Calendar 1, function #5 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1093 | 1092 | Calendar 1, function #6 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1094 | 1093 | Calendar 1, function #7 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1095 | 1094 | Calendar 1, function #8 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1096 | 1095 | Calendar 1, function #9 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1097 | 1096 | Calendar 1, function #10 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1098 | 1097
1099 | 1098
1100 | 1099
1101 | 1100
1102 | 1101
1103 | 1102
1104 | 1103
1105 | 1104
1106 | 1105
1107 | 1106
1108 | 1107 | Calendar 1, Start month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1109 | 1108 | Calendar 1, Start month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1110 | 1109 | Calendar 1, Start month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1111 | 1110 | Calendar 1, Start month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1112 | 1111 | Calendar 1, Start month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1113 | 1112 | Calendar 1, Start month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1114 | 1113 | Calendar 1, Start month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1115 | 1114 | Calendar 1, Start month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1116 | 1115 | Calendar 1, Start month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1117 | 1116 | Calendar 1, Start month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1118 | 1117 | Calendar 1, Start date #1 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1119 | 1118 | Calendar 1, Start date #2 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1120 | 1119 | Calendar 1, Start date #3 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1121 | 1120 | Calendar 1, Start date #4 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1122 | 1121 | Calendar 1, Start date #5 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1123 | 1122 | Calendar 1, Start date #6 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1124 | 1123 | Calendar 1, Start date #7 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1125 | 1124 | Calendar 1, Start date #8 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1126 | 1125 | Calendar 1, Start date #9 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1127 | 1126 | Calendar 1, Start date #10 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1128 | 1127 | Calendar 1, Start week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1129 | 1128 | Calendar 1, Start week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1130 | 1129 | Calendar 1, Start week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1131 | 1130 | Calendar 1, Start week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1132 | 1131 | Calendar 1, Start week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1133 | 1132 | Calendar 1, Start week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1134 | 1133 | Calendar 1, Start week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1135 | 1134 | Calendar 1, Start week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1136 | 1135 | Calendar 1, Start week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1137 | 1136 | Calendar 1, Start week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1138 | 1137
1139 | 1138
1140 | 1139
1141 | 1140
1142 | 1141
1143 | 1142
1144 | 1143
1145 | 1144
1146 | 1145
1147 | 1146
1148 | 1147 | Calendar 1, Stop month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1149 | 1148 | Calendar 1, Stop month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1150 | 1149 | Calendar 1, Stop month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1151 | 1150 | Calendar 1, Stop month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1152 | 1151 | Calendar 1, Stop month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1153 | 1152 | Calendar 1, Stop month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1154 | 1153 | Calendar 1, Stop month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1155 | 1154 | Calendar 1, Stop month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1156 | 1155 | Calendar 1, Stop month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1157 | 1156 | Calendar 1, Stop month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1158 | 1157 | Calendar 1, Stop date #1 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1159 | 1158 | Calendar 1, Stop date #2 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1160 | 1159 | Calendar 1, Stop date #3 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1161 | 1160 | Calendar 1, Stop date #4 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1162 | 1161 | Calendar 1, Stop date #5 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1163 | 1162 | Calendar 1, Stop date #6 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1164 | 1163 | Calendar 1, Stop date #7 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1165 | 1164 | Calendar 1, Stop date #8 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1166 | 1165 | Calendar 1, Stop date #9 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1167 | 1166 | Calendar 1, Stop date #10 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1168 | 1167 | Calendar 1, Stop week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1169 | 1168 | Calendar 1, Stop week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1170 | 1169 | Calendar 1, Stop week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1171 | 1170 | Calendar 1, Stop week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1172 | 1171 | Calendar 1, Stop week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1173 | 1172 | Calendar 1, Stop week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1174 | 1173 | Calendar 1, Stop week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1175 | 1174 | Calendar 1, Stop week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1176 | 1175 | Calendar 1, Stop week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1177 | 1176 | Calendar 1, Stop week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1178 | 1177 | Calendar 2, function #1 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1179 | 1178 | Calendar 2, function #2 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1180 | 1179 | Calendar 2, function #3 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1181 | 1180 | Calendar 2, function #4 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1182 | 1181 | Calendar 2, function #5 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1183 | 1182 | Calendar 2, function #6 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1184 | 1183 | Calendar 2, function #7 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1185 | 1184 | Calendar 2, function #8 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1186 | 1185 | Calendar 2, function #9 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1187 | 1186 | Calendar 2, function #10 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
1188 | 1187
1189 | 1188
1190 | 1189
1191 | 1190
1192 | 1191
1193 | 1192
1194 | 1193
1195 | 1194
1196 | 1195
1197 | 1196
1198 | 1197 | Calendar 2, Start month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1199 | 1198 | Calendar 2, Start month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1200 | 1199 | Calendar 2, Start month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1201 | 1200 | Calendar 2, Start month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1202 | 1201 | Calendar 2, Start month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1203 | 1202 | Calendar 2, Start month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1204 | 1203 | Calendar 2, Start month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1205 | 1204 | Calendar 2, Start month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1206 | 1205 | Calendar 2, Start month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1207 | 1206 | Calendar 2, Start month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1208 | 1207 | Calendar 2, Start date #1 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1209 | 1208 | Calendar 2, Start date #2 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1210 | 1209 | Calendar 2, Start date #3 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1211 | 1210 | Calendar 2, Start date #4 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1212 | 1211 | Calendar 2, Start date #5 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1213 | 1212 | Calendar 2, Start date #6 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1214 | 1213 | Calendar 2, Start date #7 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1215 | 1214 | Calendar 2, Start date #8 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1216 | 1215 | Calendar 2, Start date #9 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1217 | 1216 | Calendar 2, Start date #10 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
1218 | 1217 | Calendar 2, Start week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1219 | 1218 | Calendar 2, Start week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1220 | 1219 | Calendar 2, Start week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1221 | 1220 | Calendar 2, Start week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1222 | 1221 | Calendar 2, Start week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1223 | 1222 | Calendar 2, Start week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1224 | 1223 | Calendar 2, Start week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1225 | 1224 | Calendar 2, Start week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1226 | 1225 | Calendar 2, Start week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1227 | 1226 | Calendar 2, Start week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1228 | 1227
1229 | 1228
1230 | 1229
1231 | 1230
1232 | 1231
1233 | 1232
1234 | 1233
1235 | 1234
1236 | 1235
1237 | 1236
1238 | 1237 | Calendar 2, Stop month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1239 | 1238 | Calendar 2, Stop month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1240 | 1239 | Calendar 2, Stop month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1241 | 1240 | Calendar 2, Stop month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1242 | 1241 | Calendar 2, Stop month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1243 | 1242 | Calendar 2, Stop month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1244 | 1243 | Calendar 2, Stop month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1245 | 1244 | Calendar 2, Stop month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1246 | 1245 | Calendar 2, Stop month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1247 | 1246 | Calendar 2, Stop month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
1248 | 1247 | Calendar 2, Stop date #1 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1249 | 1248 | Calendar 2, Stop date #2 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1250 | 1249 | Calendar 2, Stop date #3 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1251 | 1250 | Calendar 2, Stop date #4 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1252 | 1251 | Calendar 2, Stop date #5 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1253 | 1252 | Calendar 2, Stop date #6 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1254 | 1253 | Calendar 2, Stop date #7 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1255 | 1254 | Calendar 2, Stop date #8 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1256 | 1255 | Calendar 2, Stop date #9 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1257 | 1256 | Calendar 2, Stop date #10 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
1258 | 1257 | Calendar 2, Stop week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1259 | 1258 | Calendar 2, Stop week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1260 | 1259 | Calendar 2, Stop week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1261 | 1260 | Calendar 2, Stop week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1262 | 1261 | Calendar 2, Stop week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1263 | 1262 | Calendar 2, Stop week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1264 | 1263 | Calendar 2, Stop week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1265 | 1264 | Calendar 2, Stop week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1266 | 1265 | Calendar 2, Stop week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1267 | 1266 | Calendar 2, Stop week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
1268 | 1267 | Prolonged low speed hours | Setting for prolonged external low speed operation. | 0 | 23 |  | 0 | 1.13
1269 | 1268 | Prolonged low speed minutes | Setting for prolonged external low speed operation. | 0 | 59 |  | 0 | 1.13
1270 | 1269 | Prolonged high speed hours | Setting for prolonged external high speed operation. | 0 | 23 |  | 0 | 1.13
1271 | 1270 | Prolonged high speed minutes | Setting for prolonged external high speed operation. | 0 | 59 |  | 0 | 1.13
1272 | 1271 | Exception schedule 1, Hour #1 |  | 0 | 23 | h | 0 | 1.13
1273 | 1272 | Exception schedule 1, Hour #2 |  | 0 | 23 | h | 0 | 1.13
1274 | 1273 | Exception schedule 1, Hour #3 |  | 0 | 23 | h | 0 | 1.13
1275 | 1274 | Exception schedule 1, Hour #4 |  | 0 | 23 | h | 0 | 1.13
1276 | 1275 | Exception schedule 1, Hour #5 |  | 0 | 23 | h | 0 | 1.13
1277 | 1276 | Exception schedule 1, Hour #6 |  | 0 | 23 | h | 0 | 1.13
1278 | 1277 | Exception schedule 1, Minute #1 |  | 0 | 59 | min | 0 | 1.13
1279 | 1278 | Exception schedule 1, Minute #2 |  | 0 | 59 | min | 0 | 1.13
1280 | 1279 | Exception schedule 1, Minute #3 |  | 0 | 59 | min | 0 | 1.13
1281 | 1280 | Exception schedule 1, Minute #4 |  | 0 | 59 | min | 0 | 1.13
1282 | 1281 | Exception schedule 1, Minute #5 |  | 0 | 59 | min | 0 | 1.13
1283 | 1282 | Exception schedule 1, Minute #6 |  | 0 | 59 | min | 0 | 1.13
1284 | 1283 | Exception schedule 1, Action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
1285 | 1284 | Exception schedule 1, Action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
1286 | 1285 | Exception schedule 1, Action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
1287 | 1286 | Exception schedule 1, Action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
1288 | 1287 | Exception schedule 1, Action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
1289 | 1288 | Exception schedule 1, Action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
1290 | 1289 | Exception schedule 2, Hour #1 |  | 0 | 23 | h | 0 | 1.13
1291 | 1290 | Exception schedule 2, Hour #2 |  | 0 | 23 | h | 0 | 1.13
1292 | 1291 | Exception schedule 2, Hour #3 |  | 0 | 23 | h | 0 | 1.13
1293 | 1292 | Exception schedule 2, Hour #4 |  | 0 | 23 | h | 0 | 1.13
1294 | 1293 | Exception schedule 2, Hour #5 |  | 0 | 23 | h | 0 | 1.13
1295 | 1294 | Exception schedule 2, Hour #6 |  | 0 | 23 | h | 0 | 1.13
1296 | 1295 | Exception schedule 2, Minute #1 |  | 0 | 59 | min | 0 | 1.13
1297 | 1296 | Exception schedule 2, Minute #2 |  | 0 | 59 | min | 0 | 1.13
1298 | 1297 | Exception schedule 2, Minute #3 |  | 0 | 59 | min | 0 | 1.13
1299 | 1298 | Exception schedule 2, Minute #4 |  | 0 | 59 | min | 0 | 1.13
1300 | 1299 | Exception schedule 2, Minute #5 |  | 0 | 59 | min | 0 | 1.13
1301 | 1300 | Exception schedule 2, Minute #6 |  | 0 | 59 | min | 0 | 1.13
1302 | 1301 | Exception schedule 2, Action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
1303 | 1302 | Exception schedule 2, Action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
1304 | 1303 | Exception schedule 2, Action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
1305 | 1304 | Exception schedule 2, Action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
1306 | 1305 | Exception schedule 2, Action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
1307 | 1306 | Exception schedule 2, Action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13

## Vpac 7 (RW)
GOLD_E_F_EXOline_250905
Logical var. Vpac 7 (R/W)
Index | Cell nbr | Name | Description | Min | Max | Unit | Default | Misc
Alarm settings
1 | 0 | Alarm reset | Resets all active alarms | 0 | 1 |  | 0
2 | 1
3 | 2 | Internal fire alarm function
4 | 3 | Internal fire alarm reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
5 | 4
6 | 5 |  |  | 0 | 1 |  | 0
7 | 6 | External fire alarm no. 1 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
8 | 7 | External fire alarm no. 2 reset function | 0=manual reset, 1=auto reset
9 | 8
10 | 9
11 | 10 | External alarm no. 1 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
12 | 11 | External alarm no. 2 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
13 | 12
14 | 13
15 | 14 | External alarm no. 1 input function | 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
16 | 15 | External alarm no. 2 input function | 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
17 | 16
18 | 17
19 | 18
20 | 19
21 | 20
22 | 21
23 | 22
24 | 23
25 | 24
26 | 25
27 | 26
28 | 27
Pressure sensors zero point calibration
29 | 28 | SA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
30 | 29 | EA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
31 | 30 | SA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
32 | 31 | EA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
33 | 32 | ReCO2 pressure sensor auto zero calibration |  | 0 | 1 |  | 1
34 | 33 | RHX defrost pressure sensor auto calibration |  | 0 | 1 |  | 1
35 | 34 | Carry over control pressure sensor auto calibration |  | 0 | 1 |  | 1
36 | 35 | SA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
37 | 36 | EA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
38 | 37 | SA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
39 | 38 | EA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
40 | 39 | SA end-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
41 | 40 | PX heat exchange pressure sensor auto calibration |  | 0 | 1 |  | 1 | 1.21
42 | 41 | Air quality control pressure sensor auto calibration |  | 0 | 1 |  | 1 | 2.42
43 | 42 | HC defrost sensor auto calibration |  | 0 | 1 |  | 1 | 2.42
44 | 43
45 | 44
46 | 45 | SA flow pressure sensor activate zero calibration | If value is set to 1 for min 1s calibration will be performed. | 0 | 1 |  | 0
47 | 46 | EA flow pressure sensor activate zero calibration |  | 0 | 1 |  | 0
48 | 47 | SA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
49 | 48 | EA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
50 | 49 | ReCO2 pressure sensor activate calibration |  | 0 | 1 |  | 0
51 | 50 | RHX Defrost pressure sensor activate calibration |  | 0 | 1 |  | 0
52 | 51 | Carry over control pressure sensor activate zero calibration |  | 0 | 1 |  | 0
53 | 52 | SA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
54 | 53 | EA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
55 | 54 | SA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
56 | 55 | EA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
57 | 56 | SA end-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
58 | 57 | PX heat exchange pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 1.21
59 | 58 | Air quality control pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 2.42
60 | 59 | HC defrost pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 2.42
61 | 60
62 | 61
AHU external sensors
162 | 161 | External room sensor 1 function |  | 0 | 1 |  | 0
163 | 162 | External room sensor 2 function |  | 0 | 1 |  | 0
164 | 163 | External room sensor 3 function |  | 0 | 1 |  | 0
165 | 164 | External room sensor 4 function |  | 0 | 1 |  | 0
166 | 165
167 | 166 | External room temp from BMS function |  | 0 | 1 |  | 0
168 | 167
169 | 168
170 | 169
171 | 170
172 | 171 | External OA sensor 1 function |  | 0 | 1 |  | 0
173 | 172 | External OA sensor 2 function |  | 0 | 1 |  | 0
174 | 173 | External OA sensor 3 function |  | 0 | 1 |  | 0
175 | 174 | External OA sensor 4 function |  | 0 | 1 |  | 0
176 | 175
177 | 176 | External OA temp from BMS function |  | 0 | 1 |  | 0
AHU Heat exchange
182 | 181 | RHX defrost function | Setting for activating the defrost function for the rotary heat exchanger. | 0 | 1 |  | 0
183 | 182 | RHX defrost calibration |  | 0 | 1 |  | 0
184 | 183
185 | 184
186 | 185
187 | 186 | RHX carry over control function | Setting for activating the carry over control function for the rotary heat exchanger. | 0 | 1 |  | 0
188 | 187
189 | 188
190 | 189 | RHX min exhaust air temp function |  | 0 | 1 |  | 0
191 | 190
192 | 191
193 | 192
194 | 193
195 | 194
196 | 195
197 | 196
198 | 197 | PHX periodic operation of bypass damper function |  | 0 | 1 |  | 1
199 | 198
200 | 199
201 | 200 | PHX Bypass optimize |  | 0 | 1 |  | 0 | 1.13
202 | 201
203 | 202
204 | 203
205 | 204 | CHX periodic operation of pump function |  | 0 | 1 |  | 1
206 | 205 | CHX periodic operation of valve function |  | 0 | 1 |  | 1
AHU Heat/Cool
228 | 227 | Re-heat periodic operation of pump function |  | 0 | 1 |  | 1
229 | 228 | Re-heat periodic operation of valve function |  | 0 | 1 |  | 1
230 | 229
231 | 230
232 | 231
233 | 232
234 | 233
235 | 234
236 | 235
237 | 236
238 | 237
239 | 238
240 | 239
241 | 240
242 | 241
243 | 242
244 | 243
245 | 244 | Extra regulation 1 periodic operation of pump function |  | 0 | 1 |  | 1
246 | 245 | Extra regulation 1 periodic operation of valve function |  | 0 | 1 |  | 1
247 | 246
248 | 247
249 | 248
250 | 249
251 | 250
252 | 251
253 | 252
254 | 253
255 | 254
256 | 255
257 | 256
258 | 257
259 | 258
260 | 259
261 | 260
262 | 261
263 | 262
264 | 263
265 | 264
266 | 265
267 | 266
268 | 267
269 | 268
270 | 269
271 | 270
272 | 271
273 | 272
274 | 273 | Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
275 | 274 | Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
276 | 275 | Cool periodic operation of valve function |  | 0 | 1 |  | 0
Summer night cool/Intermittent night heat /Morning boost
284 | 283 | Summer night cool function | Moved to Vpac 6, 284 | 0 | 1 |  | 0
285 | 284
286 | 285
287 | 286
288 | 287
289 | 288
290 | 289
291 | 290
292 | 291
293 | 292
294 | 293
295 | 294
296 | 295 | Intermittent night heat function |  | 0 | 1 |  | 0
297 | 296
298 | 297
299 | 298
300 | 299
301 | 300
302 | 301 | Intermittent night heat recirculation function |  | 0 | 1 |  | 1 | 1.12
303 | 302
304 | 303
305 | 304 | Morning boost function |  | 0 | 1 |  | 0
Heating boost
320 | 319 | Heating boost function |  | 0 | 1 |  | 0
321 | 320
322 | 321
Xzone function
325 | 324 | Xzone heat function |  | 0 | 1 |  | 0
326 | 325
327 | 326 | Xzone cool function |  | 0 | 1 |  | 0
328 | 327
Xzone external sensors
374 | 373 | Xzone external room sensor 1 function |  | 0 | 1 |  | 0
375 | 374 | Xzone external room sensor 2 function |  | 0 | 1 |  | 0
376 | 375 | Xzone external room sensor 3 function |  | 0 | 1 |  | 0
377 | 376 | Xzone external room sensor 4 function |  | 0 | 1 |  | 0
378 | 377
379 | 378 | Xzone external room temp from BMS function |  | 0 | 1 |  | 0
380 | 379
381 | 380
382 | 381
383 | 382
Xzone Heat/Cool
384 | 383
385 | 384
386 | 385 | Xzone reheat periodic operation of pump function |  | 0 | 1 |  | 1
387 | 386 | Xzone reheat periodic operation of valve function |  | 0 | 1 |  | 1
388 | 387
389 | 388
390 | 389
391 | 390
392 | 391
393 | 392
394 | 393
395 | 394
396 | 395
397 | 396
398 | 397
399 | 398
400 | 399 | Xzone Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
401 | 400 | Xzone Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
402 | 401 | Xzone Cool periodic operation of valve function |  | 0 | 1 |  | 0
403 | 402
404 | 403
405 | 404
406 | 405
407 | 406
408 | 407
409 | 408
Pre-heat
410 | 409 | Pre-heat function |  | 0 | 1 |  | 0
411 | 410
412 | 411
413 | 412
414 | 413 | Pre-heat periodic operation of pump function |  | 0 | 1 |  | 1
415 | 414 | Pre-heat periodic operation of valve function |  | 0 | 1 |  | 1
416 | 415
417 | 416
418 | 417
419 | 418
420 | 419
421 | 420
422 | 421
ReCO2
423 | 422
424 | 423
425 | 424 | ReCO2 Calibration |  | 0 | 1 |  | 0
426 | 425
427 | 426
428 | 427
429 | 428
430 | 429
431 | 430
432 | 431
433 | 432
434 | 433
435 | 434
436 | 435
437 | 436
438 | 437
439 | 438
440 | 439
Humidity/VOC
441 | 440
442 | 441
443 | 442
444 | 443
445 | 444
446 | 445
447 | 446
448 | 447
449 | 448
450 | 449
451 | 450
452 | 451
453 | 452
454 | 453
455 | 454
456 | 455
457 | 456 | Dehumidifying function | Moved to Vpac 6 index 457 | 0 | 1 |  | 1 | 1.12
458 | 457
459 | 458 | Heat exchange active in dehumidifying sequence |  | 0 | 1 |  | 0
460 | 459
461 | 460
462 | 461
463 | 462
464 | 463
465 | 464 | VOC sensor function | Moved to Vpac 6 index 465 | 0 | 1 |  | 0 | 1.23
466 | 465
467 | 466
468 | 467
Exhaust heat
477 | 476 | Exhaust heat periodic operation of pump function | Exhaust heat periodic operation of pump function | 0 | 1 |  | 1 | 2.43
478 | 477 | Exhaust heat periodic operation of valve function | Exhaust heat periodic operation of valve function | 0 | 1 |  | 1 | 2.43
SMART Link
489 | 488 | SMART Link WB Cooling Optimize function |  | 0 | 1 |  | 0 | 1.26
490 | 489 | SMART Link WB Heating Optimize function |  | 0 | 1 |  | 0
491 | 490
492 | 491
493 | 492
494 | 493
495 | 494
496 | 495
497 | 496
498 | 497
499 | 498
500 | 499
501 | 500
502 | 501
503 | 502
504 | 503 | AQUA Link Function |  | 0 | 1
AYC
521 | 520
522 | 521
523 | 522
524 | 523
525 | 524
526 | 525
527 | 526
528 | 527
529 | 528
530 | 529 | AYC Heated water periodic operation of pump |  | 0 | 1 |  | 1
531 | 530 | AYC Heated water periodic operation of valve |  |  | 1 |  | 0
532 | 531
533 | 532
534 | 533
535 | 534
536 | 535 | AYC Heated water OA temp compensation |  | 0 | 1 |  | 0
537 | 536
538 | 537
539 | 538
540 | 539
541 | 540
542 | 541
543 | 542
544 | 543
545 | 544
546 | 545
547 | 546 | AYC Heated water room temp compensation function |  | 0 | 1 |  | 0
548 | 547 | AYC Heated water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
549 | 548
550 | 549
551 | 550
552 | 551
553 | 552 | AYC Heated water night temp compensation function |  | 0 | 1 |  | 0
554 | 553
555 | 554
556 | 555
557 | 556
558 | 557
559 | 558
560 | 559
561 | 560
562 | 561
563 | 562
564 | 563
565 | 564
566 | 565
567 | 566
568 | 567
569 | 568
570 | 569
571 | 570
572 | 571
573 | 572
574 | 573
575 | 574
576 | 575
577 | 576
578 | 577
579 | 578 | AYC Chilled water periodic operation of pump |  | 0 | 1 |  | 1
580 | 579 | AYC Chilled water periodic operation of valve |  |  | 1 |  | 0
581 | 580
582 | 581
583 | 582
584 | 583
585 | 584 | AYC Chilled water OA temp compensation |  | 0 | 1 |  | 0
586 | 585
587 | 586
588 | 587
589 | 588
590 | 589
591 | 590
592 | 591
593 | 592
594 | 593
595 | 594
596 | 595 | AYC Chilled water room temp compensation function |  | 0 | 1 |  | 0
597 | 596 | AYC Chilled water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
598 | 597
599 | 598
600 | 599
601 | 600
602 | 601 | AYC Chilled water night temp compensation function |  | 0 | 1 |  | 0
603 | 602
604 | 603
605 | 604
606 | 605
607 | 606
608 | 607
609 | 608
610 | 609
611 | 610
612 | 611
613 | 612
614 | 613
615 | 614
616 | 615
617 | 616
618 | 617 | AYC Chilled water dew point compensation air flow boost |  | 0 | 1 |  | 0
619 | 618
620 | 619
621 | 620
622 | 621
623 | 622
624 | 623
625 | 624
626 | 625
627 | 626
628 | 627
629 | 628
630 | 629
631 | 630
632 | 631
633 | 632
634 | 633
635 | 634
636 | 635
Optimize
637 | 636 | Optimize function |  | 0 | 1 |  | 0
Reserved
824 | 823 | Extra regulation 2 periodic operation of pump function |  | 0 | 1 |  | 1 | 1.13
825 | 824 | Extra regulation 2 periodic operation of valve function |  | 0 | 1 |  | 1 | 1.13
Time schedule
933 | 932 | Effective period always | 0=Off, 1=On | 0 | 1 |  | 1
BMS I/O-modules
1000 | 999 | External operation I/O-module A, function |  | 0 | 1 |  | 0 | 1.20
1001 | 1000 | External operation I/O-module A, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
1002 | 1001 | External operation I/O-module A, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
1003 | 1002 | External operation I/O-module A, digital output |  | 0 | 1 |  | 0 | 1.20
1004 | 1003 | External operation I/O-module B, function |  | 0 | 1 |  | 0 | 1.20
1005 | 1004 | External operation I/O-module B, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
1006 | 1005 | External operation I/O-module B, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
1007 | 1006 | External operation I/O-module B, digital output |  | 0 | 1 |  | 0 | 1.20
1008 | 1007 | External operation I/O-module C, function |  | 0 | 1 |  | 0 | 1.20
1009 | 1008 | External operation I/O-module C, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
1010 | 1009 | External operation I/O-module C, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
1011 | 1010 | External operation I/O-module C, digital output |  | 0 | 1 |  | 0 | 1.20