## Overview_data
GB.BACnet480.100915
BACnet IP
GOLD sizes 04-80, program version 5.15 and newer versions.
Overview
This BACnet driver is implemented in GOLD PV 5.15 and provides the function
of monitoring and operating the air handling unit.
GOLD is a BACnet Application Specific Controller (B-ASC).
The supported Data Link Layer Options are BACnet / IP.
See also document BACnet PICS (Protocol Implementation Conformance Statement) GOLD
and GOLD EDE (Engineering Data Exchange).
BACnet Interoperability Building Blocks Supported.
Data Sharing |  | DS-RP-B | Data Sharing-Read Property-B
Data Sharing |  | DS-RPM-B | Data Sharing-Read Property Multiple-B
Data Sharing |  | DS-WP-B | Data Sharing-Write Property-B
Data Sharing |  | DS-COV-B | Data Sharing-COV-B
Alarm&Event Management |  | AE-N-I-B | Alarm&Event-Notification Internal-B
Device Management |  | DM-DDB-B | Device Management-Dynamic Device Binding-B
Device Management |  | DM-DOB-B | Device Management-Dynamic Object Binding-B
Device Management |  | DM-DCC-B | Device Management-Dynamic Communication Control-B
Standard Object Types Supported.
Object Type | Properties
Analog Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, COV_Increment.
Analog Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Priority_Array, Relinquish_Default, COV_Increment.
Binary Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Polarity, Time_Delay, Notification_Class, Alarm_Value, Event_Enable, Acked_Transitions, Notify_Type, Event_Time_Stamps.
Binary Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Priority_Array, Relinquish_Default.
Device | Object_Identifier, Object_Name, Object_Type, System_Status, Vendor_Name, Vendor_Identifier, Model_Name, Firmware_Revision, Application_Software_Version, Location, Description, Protocol_Version, Protocol_Revision, Protocol_Services_Supported, Protocol_Object_Types_Supported, Object_List, Max_APDU_Length_Accepted, Segmentation_Supported, APDU_Timeout, Number_Of_APDU_Retries, Device_Address_Binding, Database_Revision, Active_COV_Subscriptions.
Notification Class | Object_Identifier, Object_Name, Object_Type, Description, Notification_Class, Priority, Ack_Required, Recipient_List, Profile_Name.

## Overview parameters
GB.BACnet480.100915
Operation mode 1 |  | AI 84 |  | Extract air filter pressure level |  | AI 52 |  | EA/Room temperature |  | AI 28
Communication operation mode |  | AV 174 |  | EA filter pressure level limit |  | AI 53 |  | EA/Room temperature setpoint |  | AV 41
Operation mode 2 |  | AI 85 | [5 empty] | SA Min temperature setpoint |  | AV 42
Operation output |  | BI 7 | [5 empty] | SA Max temperature setpoint |  | AV 43
Low speed output |  | BI 3 |  |  | EA Duct pressure |  | AI 6
High speed output |  | BI 4 |  |  | EA Low speed pressure setpoint |  | AV 12
Damper output |  | BI 8 |  |  | EA High speed pressure setpoint |  | AV 13 | SA Duct Pressure |  | AI 4
Present tripped alarm |  | AI 78 | [5 empty] | SA Low speed pressure setpoint |  | AV 8
A-alarm |  | BI 5 | [5 empty] | SA High speed pressure setpoint |  | AV 9
B-alarm |  | BI 6
Alarm reset |  | BV 0
[8 empty] | SA Temperature |  | AI 27
[8 empty] | SA Temperature setpoint |  | AV 40
EA Airflow |  | AI 2 | [5 empty] | ERS 1 Diff |  | AV 32
EA Fan level |  | AI 13
EA Low speed airflow setpoint |  | AV 4
EA High speed airflow setpoint |  | AV 5
Outdoor temperature |  | AI 29
Supply air filter pressure level |  | AI 49
SA filter pressure level limit |  | AI 50
Heat exchange regulator |  | AI 90
| SA Airflow |  | AI 0 |  | Reheat level |  | AI 36 | Cooling level |  | AI 39
| SA Fan level |  | AI 12 |  | Heat output |  | BI 0 | Cool output 1 |  | BI 1
| SA Low speed airflow setpoint |  | AV 0 |  | Anti frost temperature |  | AI 32 | Cool output 2 |  | BI 2
| SA High speed airflow setpoint |  | AV 1

## Analog Inputs
GB.BACnet480.100915
Analog Inputs (RO).
Object Instance | Object Name | Min/Max | Misc
0 | SA Airflow | 0-8200l/s
Present supply airflow.
1 | SA Airflow regulator | 0-8200l/s
Present supply airflow regulator setpoint.
2 | EA Airflow | 0-8200l/s
Present extract airflow.
3 | EA Airflow regulator | 0-8200l/s
Present extract airflow regulator setpoint.
4 | SA Duct pressure | 0-2000Pa
Present supply air duct pressure.
5 | SA Duct pressure regulator | 0-2000Pa
Present supply air duct pressure regulator setpoint.
6 | EA Duct pressure | 0-2000Pa
Present extract air duct pressure.
7 | EA Duct pressure regulator | 0-2000Pa
Present extract air duct pressure regulator setpoint.
8 | SA VAV demand/boost input | 0-100.00%
Present input signal for supply air VAV demand or boosting function.
9 | SA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
10 | EA VAV demand/boost input | 0-100.00%
Present input signal for extract air VAV demand or boosting function.
11 | EA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
12 | SA Fan level | 0-100.00%
Present running level for the supply air fan.
13 | EA Fan level | 0-100.00%
Present running level for the extract air fan.
14 | SA Fan effect | 0-6500W
Present power consumption level for the supply air fan.
15 | EA Fan effect | 0-6500W
Present power consumption level for the extract air fan.
16 | SFP | 0.0-9.9
SFP supply air + extract air.
17 | SA Frequency | 0-100.00Hz
Present frequency level for the supply air fan.
18 | EA Frequency | 0-100.00Hz
Present frequency level for the extract air fan.
19 | SA Voltage | 0-500V
Present voltage level for the supply air fan.
20 | EA Voltage | 0-500V
Present voltage level for the extract air fan.
21 | SA Current | 0-30.000A
Present current level for the supply air fan.
22 | EA Current | 0-30.000A
Present current level for the extract air fan.
23 | SA Airflow pressure | 0-2000Pa
Present airflow pressure in the supply air fan inlet.
24 | EA Airflow pressure | 0-2000Pa
Present airflow pressure in the extract air fan inlet.
25 | SA Temp regulator | -55.00-125.00°C
Present supply air temperature regulator setpoint.
26 | EA Temp regulator | -55.00-125.00°C
Present extract air temperature regulator setpoint.
27 | SA Temperature | -55.00-125.00°C
Present supply air temperature.
28 | EA/Room temperature | -55.00-125.00°C
Present extract air/room temperature in the unit.
29 | Outdoor temperatur | -55.00-125.00°C
Present outdoor air temperature in the unit.
30 | EA/Room temperature external | -55.00-125.00°C
Present room temperature external from the unit.
31 | Outdoor temperatur external | -55.00-125.00°C
Present outdoor air temperature external from the unit.
32 | Anti frost temperature | -55.00-125.00°C
Present anti frost temperature for water reheating coils.
33 | Temperature sensor 3 | -55.00-125.00°C
Present temperature for temp sensor no.3
34 | Temperature sensor 4 | -55.00-125.00°C
Present temperature for temp sensor no.4
35 | Rotary heat exchanger level | 0-100.00%
Present operation level from rotary heat exchanger.
36 | Reheat level | 0-100.00%
Present level of reheat.
37 | SA Down regulation level | 0-100.00%
Present level of supply airflow down regulation.
38 | Extre regulation sequence level | 0-100.00%
Present level of the extra regulation sequence.
39 | Cooling level | 0-100.00%
Present level of cooling.
40 | Heating boost level | 0-100.00%
Present level of heating boost.
41 | Cooling boost level | 0-100.00%
Present level of cooling boost.
42 | HX pressure level | 0-2000Pa
Present pressure drop for the rotary heat exchanger.
43 | HX pressure alarm limit | 0-2000Pa
Present pressure drop alarm limit for the rotary heat exchanger.
44 | HX temperature | 0-100.00°C
Present temperature inside the control unit for the rotary heat exchanger.
45 | Effect reduction level | 0-100.00%
Present level of max output signal for electrical reheaters, active during low supply airflow.
46 | Anti frost temp setpoint/operation | 10.00-16.00°C
Present anti frost temperature setpoint for water reheating coils during unit operation.
47 | Anti frost temp setpoint/stop | 15.00-40.00°C
Present anti frost temperature setpoint for water reheating coils when the unit is in stop.
48 | Anti frost temp alarm limit | 5.00-30.00°C
Setting of antifrost temperature alarm limit.
49 | Supply air filter pressure level | 0-2000Pa
Present supply air filter pressure drop.
50 | Supply air filter pressure alarm limit. | 0-2000Pa
Present supply air filter pressure alarm limit.
51 | Supply air filter pressure level, new | 0-2000Pa
Supply air filter pressure saved from calibration.
52 | Extract air filter pressure level | 0-2000Pa
Present extract air filter pressure drop.
53 | Extract air filter pressure alarm limit. | 0-2000Pa
Present extract air filter pressure alarm limit.
54 | Extract air filter pressure level, new | 0-2000Pa
Extract air filter pressure saved from calibration.
55 | Temperature displacement | -5.00 - 5.00°C
Present temperature displacement from input signal.
56 | Coil type | 0-20
Present connected reheat coil type.
57 | Cool step time | 0-600s
Present time between cool step shift.
58 | Cool relay 1 restart time | 0-900s
Present time between two starts of cool relay 1.
59 | Cool relay 2 restart time | 0-900s
Present time between two starts of cool relay 2.
60 | Programversion, HMI | 0-10.00
Present programversion for the handterminal.
61 | Programversion, HMI-slave | 0-10.00
Present programversion for the extra handterminal.
62 | Programversion, main controller. | 0-10.00
Present programversion for the main control unit.
63 | Programversion, SA FC-1. | 0-10.00
Present programversion for the supply air frequency converter no.1.
64 | Programversion, SA FC-2. | 0-10.00
Present programversion for the supply air frequency converter no.2.
65 | Programversion, EA FC-1. | 0-10.00
Present programversion for the extract air frequency converter no.1.
66 | Programversion, EA FC-2. | 0-10.00
Present programversion for the extract air frequency converter no.2.
67 | Programversion, HX control unit | 0-10.00
Present programversion for the rotary heat exchange control unit.
68 | Weekday | 0 - 6
Present weekday for the unit's internal clock.
69 | Extended low speed op. Hours | 0-23
Present time for extended low speed operation.
70 | Extended low speed op. Minutes | 0-59
Present time for extended low speed operation.
71 | Extended high speed op. Hours | 0-23
Present time for extended high speed operation.
72 | Extended high speed op. Minutes | 0-59
Present time for extended high speed operation.
73 | SA Fan operation time | 0-9999
Present operation time for the supply air fan, measured in minutes and present in days (24h).
74 | EA Fan operation time | 0-9999
Present operation time for the extract air fan, measured in minutes and present in days (24h).
75 | Cool operation time | 0-9999
Present operation time for cooling, measured in minutes and present in days (24h).
76 | Heat exchange operation time | 0-9999
Present operation time for heat exchange, measured in minutes and present in days (24h).
77 | Reheat operation time | 0-9999
Present operation time for reheat, measured in minutes and present in days (24h).
78 | Present tripped alarm | 0-200
Present tripped alarm number with highest priority.
79 | Active not tripped alarm no.1 | 0-200
Present active alarm in delay.
80 | Active not tripped alarm no.2 | 0-200
Present active alarm in delay.
81 | Active not tripped alarm no.3 | 0-200
Present active alarm in delay.
82 | SA Fan size | 04 - 80
Present supply air fan size.
83 | EA Fan size | 04 - 80
Present extract air fan size.
84 | Operation mode 1 | 0 - 18
0=Manual stop. 1=Ext. stop. 2=Com. stop 1. 3=Manual high speed. 4=Summer night cooling. 5=Int. night heat. 6=Manual low speed. 7=Ext. high speed. 8=Com. high speed. 9=Year channel stop. 10=Year channel high speed. 11=Year channel low speed. 12=Time channel high speed. 13=Ext. low speed. 14=Com. low speed. 15=Time channel low speed. 16=Time channel stop. 17=Low speed=stop. 18=Com. stop 2. (New in PV 5.00)
85 | Operation mode 2 | 0 - 22
0= 1=Coold air recovery. 2=Cooling boost. 3=SA down regulation. 4=HX defrosting. 5=Anti frost func. active. 6=Effect reduction. 7=Startup. 8=Zero calibration. 9=Extended low speed. 10=Extended high speed. 11=Air adjustment. 12=Cooling off. 13=Purging R.HX. 14=Extended R.HX. op. 15=Filter calibration. 16=R.HX. calibration 17=Morning boost. 18=Heating boost. 19=Alarm. 20=CoolDX pressure reduction. (PV 2.00) 21=Startup extract air fan (New in 4.00) R.HX speed limited. (Only in PV 2.00-2.02) 22=Fan heat retention (New in PV 5.00)
86 | Operation mode, manual | 0 - 3
Present manual operation set on the unit's handterminal. 0=Stop. 1=Auto operation. 2=Manual low speed. 3=Manual high speed.
87 | Copy of Input Status 1-16. | 0-65535
Bit 0=1x0001 Bit 1=1x0002 Bit 15=1x0016
88 | Copy of Input Status 17-32. | 0-65535
Bit 0=1x00017 Bit 1=1x00018 Bit 15=1x0032
89 | Copy of Input Status 33-48. | 0-65535
Bit 0=1x00033 Bit 1=1x00034 Bit 15=1x0048
90 | Heat exchanger regulator | 0-100.00%
Present level of heat exchanger regulator RX/CX/PX.
91 | Extract air-humidity | 0-100.00%
Present level of extract air-humidity.
92 | Extract air-humidity temperature | -55.00-125.00°C
Present temperature inside extract air-humidity sensor.
93 | Extract air-dewpoint | -55.00-125.00°C
Calculated extract air-dewpoint.
94 | AYC chilled water temperature | -55.00-125.00°C
Present AYC chilled water temperature.
95 | AYC chilled water temperature regulator | -55.00-125.00°C
Present AYC chilled water temperature regulator setpoint.
96 | AYC chilled water output | 0-100.00%
Present level of AYC chilled water valve output.
97 | Supply air-dewpoint regulator | -55.00-125.00°C
Present supply air-dewpoint regulator setpoint.
98 | Supply air-humidity | 0-100.00%
Present level of supply air-humidity
99 | Supply air-humidity temperature | -55.00-125.00°C
Present temperature inside supply air-humidity sensor.
100 | Supply air-dewpoint | -55.00-125.00°C
Calculated supply air-dewpoint.
101 | C.HX. Temperature | -55.00-125.00°C
Present temperature of coil heat exchanger.
102 | P.HX. Temperature 1 | -55.00-125.00°C
Present temperature 1 of plate heat exchanger.
103 | P.HX. Temperature 2 | -55.00-125.00°C
Present temperature 2 of plate heat exchanger.
104 | P/C.HX. Humidity | 0-100.00%
Present level of air-humidity in plate/coil heat exchanger.
105 | R.HX. Efficiency | 0-100.00%
Calculated level of rotary heat exchanger efficiency.
106 | C.HX. Valve output | 0-100.00%
Present level of coil heat exchanger valve output.
107 | P.HX bypass output | 0-100.00%
Present level of plate heat exchanger bypass output.
108 | Supply air prefilter pressure level | 0-2000Pa
Present supply air prefilter pressure drop.
109 | Supply air prefilter pressure alarm limit. | 0-2000Pa
Present supply air prefilter pressure alarm limit.
110 | Supply air prefilter pressure level, new | 0-2000Pa
Supply air prefilter pressure saved from calibration.
111 | Extract air prefilter pressure level | 0-2000Pa
Present extract air prefilter pressure drop.
112 | Extract air prefilter pressure alarm limit. | 0-2000Pa
Present extract air prefilter pressure alarm limit.
113 | Extract air prefilter pressure level, new | 0-2000Pa
Extract air prefilter pressure saved from calibration.
114 | Xzone reheat level | 0-100.00%
Present level of Xzone reheat.
115 | Xzone anti frost temperature | -55.00-125.00°C
Present Xzone anti frost temperature for water reheating coils.
116 | Xzone cooling level | 0-100.00%
Present level of Xzone cooling.
117 | Xzone cool step time | 0-600s
Present time between Xzone cool step shift.
118 | Xzone cool relay 1 restart time | 0-900s
Present time between two starts of Xzone cool relay 1.
119 | Xzone cool relay 2 restart time | 0-900s
Present time between two starts of Xzone cool relay 2.
120 | Xzone SA Temp regulator | -55.00-125.00°C
Present Xzone supply air temperature regulator setpoint.
121 | Xzone EA Temp regulator | -55.00-125.00°C
Present Xzone extract air temperature regulator setpoint.
122 | Xzone SA Temperature | -55.00-125.00°C
Present Xzone supply air temperature.
123 | Xzone EA/Room temperature | -55.00-125.00°C
Present Xzone extract air/room temperature.
124 | Pre-heating air temperature | -55.00-125.00°C
Present pre-heating air temperature.
125 | Pre-heating level | 0-100.00%
Present level of pre-heating.
126 | Pre-heating anti frost temperature | -55.00-125.00°C
Present anti frost temperature for water pre-heating coils.
127 | ReCO2 CO2 input | 0-100.00%
Present input signal for ReCO2 CO2.
128 | ReCO2 internal damper output | 0-100.00%
Present output signal for ReCO2 internal damper.
129 | ReCO2 external damper output | 0-100.00%
Present output signal for ReCO2 external damper.
130 | ReCO2 outdoor airflow | 0-8200l/s
Present ReCO2 outdoor airflow.
131 | ReCO2 outdoor airflow regulator | 0-8200l/s
Present ReCO2 outdoor airflow regulator setpoint.
132 | ReCO2 outdoor airflow pressure | 0-2000Pa
Present ReCO2 outdoor airflow pressure.
133 | Preheat operation time | 0-9999
Present operation time for preheat, measured in minutes and present in days (24h).
134 | Xzone cool operation time | 0-9999
Present operation time for Xzone cooling, measured in minutes and present in days (24h).
135 | Xzone reheat operation time | 0-9999
Present operation time for Xzone reheat, measured in minutes and present in days (24h).
136 | Supply air-D temperature | -55.00-125.00°C
Present supply air-D temperature.
137 | Extract air-D temperature | -55.00-125.00°C
Present extract air-D temperature.
138 | AYC heat temperature | -55.00-125.00°C
Present AYC heat temperature.
139 | AYC heat temp regulator | -55.00-125.00°C
Present AYC heat temperature regulator setpoint.
140 | AYC heat valve output | 0-100.00%
Present level of AYC heat valve output.
141 | Min/Max/Average Sens1Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 1 temperature.
142 | Min/Max/Average Sens2Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 2 temperature.
143 | Min/Max/Average Sens3Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 3 temperature.
144 | Min/Max/Average Sens4Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 4 temperature.

## Analog Value
GB.BACnet480.100915
Analog Value (R/W).
Object Instance | Object Name | Min/Max | Misc
0 | SA Low speed airflow setpoint | 0-8200l/s
Supply airflow setpoint for the unit when running in low speed operation.
1 | SA High speed airflow setpoint | 0-8200l/s
Supply airflow setpoint for the unit when running in high speed operation.
2 | SA Max speed airflow setpoint | 0-8200l/s
Supply airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
3 | SA Min speed airflow setpoint | 0-8200l/s
Supply airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
4 | EA Low speed airflow setpoint | 0-8200l/s
Extract airflow setpoint for the unit when running in low speed operation.
5 | EA High speed airflow setpoint | 0-8200l/s
Extract airflow setpoint for the unit when running in high speed operation.
6 | EA Max speed airflow setpoint | 0-8200l/s
Extract airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
7 | EA Min speed airflow setpoint | 0-8200l/s
Extract airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
8 | SA Low speed pressure setpoint | 0-750Pa
Supply air duct pressure setpoint for the unit when running in low speed operation.
9 | SA High speed pressure setpoint | 20-750Pa
Supply air duct pressure for the unit when running in high speed operation.
10 | SA Max speed output signal | 10.00-100.00%
Max. limit for the supply air fan speed when running in pressure regulation mode.
11 | SA Max speed pressure setpoint | 20-750Pa
Supply air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
12 | EA Low speed pressure setpoint | 0-750Pa
Extract air duct pressure setpoint for the unit when running in low speed operation.
13 | EA High speed pressure setpoint | 20-750Pa
Extract air duct pressure setpoint for the unit when running in high speed operation.
14 | EA Max speed output signal | 10.00-100.00%
Max. limit for the extract air fan speed when running in pressure regulation mode.
15 | EA Max speed pressure setpoint | 20-750Pa
Extract air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
16 | SA Low speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 30..31 for the unit when running in low speed operation.
17 | SA High speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 30..31 for the unit when running in high speed operation.
18 | EA Low speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 32..33 for the unit when running in low speed operation.
19 | EA High speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 32..33 for the unit when running in high speed operation.
20 | SA Airflow regulation zone | 1.00 - 10.00
Supply airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
21 | SA Airflow C-factor | 0.005 - 2.500
Supply airflow regulator affection setting.
22 | EA Airflow regulation zone | 1.00 - 10.00
Extract airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
23 | EA Airflow C-factor | 0.005 - 2.500
Extract airflow regulator affection setting.
24 | SA Pressure regulation zone | 1.00 - 10.00
Supply air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
25 | SA Pressure C-factor | 0.005 - 2.500
Supply air pressure regulator affection setting.
26 | EA Pressure regulation zone | 1.00 - 10.00
Extract air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
27 | EA Pressure C-factor | 0.005 - 2.500
Extract air pressure regulator affection setting.
28 | SA Demand P-band. | 1.00 - 100.00
Supply air demand regulator P-band setting.
29 | SA Demand C-factor | 0.005 - 2.500
Supply air demand regulator affection setting.
30 | EA Demand P-band. | 1.00 - 100.00
Extract air demand regulator P-band setting.
31 | EA Demand C-factor | 0.005 - 2.500
Extract air demand regulator affection setting.
32 | ERS 1 Diff | 1.00 - 7.00°C
Supply air temperature difference setting accordning to the diagram for ERS 1.
33 | ERS 1 Breakpoint | 12.00 - 26.00°C
Breakpoint setting accordning to the diagram for ERS 1.
34 | ERS 2 Breakpoint X1 | 10.00-38.00°C
Breakpoint X1 setting accordning to the diagram for ERS 2.
35 | ERS 2 Breakpoint Y1 | 10.00-40.00°C
Breakpoint Y1 setting accordning to the diagram for ERS 2.
36 | ERS 2 Breakpoint X2 | 11.00-39.00°C
Breakpoint X2 setting accordning to the diagram for ERS 2.
37 | ERS 2 Breakpoint Y2 | 10.00-40.00°C
Breakpoint Y2 setting accordning to the diagram for ERS 2.
38 | ERS 2 Breakpoint X3 | 12.00-40.00°C
Breakpoint X3 setting accordning to the diagram for ERS 2.
39 | ERS 2 Breakpoint Y3 | 10.00-40.00°C
Breakpoint Y3 setting accordning to the diagram for ERS 2.
40 | SA Temperature setpoint | 10.00-40.00°C
Supply air temperature setting, for supply air temp regulation mode.
41 | EA/Room Temperature setpoint | 10.00-40.00°C
Extract air/room temperature setting, for Extract air/room temp regulation mode.
42 | SA Min temp setpoint | 8.00-20.00°C
Supply air min.setpoint during EA/room regulation mode.
43 | SA Max temp setpoint | 16.00-50.00°C
Supply air max.setpoint during EA/room regulation mode.
44 | SA Temperature P-band | 1.00 - 40.00
Supply air temperature regulator P-band setting.
45 | EA/Room Temperature P-band | 1.00 - 40.00
Extract air/room temperature regulator P-band setting.
46 | SA HX. Reg C-factor | 0.000 - 2.500
Supply air heat exchange regulator affection setting.
47 | EA/Room HX. Reg C-factor | 0.000 - 2.500
Extract air/room heat exchange regulator affection setting.
48 | SA Heat Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
49 | EA/Room Heat Reg C-factor | 0.000 - 2.500
Extract air/room reheat regulator affection setting.
50 | SA Extra Reg heat C-factor | 0.000 - 2.500
Supply air extra regulation sequence for reheating regulator affection setting.
51 | SA Extra Reg cool C-factor | 0.000 - 2.500
Supply air extra regulation sequence for cooling regulator affection setting.
52 | EA Extra Reg heat C-factor | 0.000 - 2.500
Extract air extra regulation sequence for reheating regulator affection setting.
53 | EA Extra Reg cool C-factor | 0.000 - 2.500
Extract air extra regulation sequence for cooling regulator affection setting.
54 | SA Down regulation Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
55 | Reserve AV1
56 | SA Cool reg C-factor | 0.000 - 2.500
Supply air cool regulator affection setting.
57 | EA/Room Cool reg C-factor | 0.000 - 2.500
Extract air/room cool regulator affection setting.
58 | SA Cooling boost C-factor | 0.000 - 2.500
Supply air cooling boost affection setting.
59 | EA/Room Cooling boost reg C-factor | 0.000 - 2.500
Extract air/room cooling boost regulator affection setting.
60 | HX Pressure alarm set. | 30 - 100Pa
Heat exchange pressure alarm limit setting (alarm no.38).
61 | P/C.HX. defrost P-band | 1.00 - 40.00
Plate/coil heat exchange defrost P-band setting.
62 | P/C.HX. defrost C-factor | 0.000 - 2.500
Plate/coil heat exchange defrost C-factor setting.
63 | Cooling off set. | 10 - 50%
Cooling off airflow setting in % of max. airflow.
64 | SA Down regulation neautral zone | 0.00-10.00°C
Neutral zone setting before downregulation is permitted.
65 | Cool Outdoor temp limit.1 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 1.
66 | Cool Outdoor temp limit.2 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 2.
67 | Cool Outdoor temp limit.3 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 3.
68 | Temperature reg. Neutral zone | 0.50-10.00°C
Neutral zone setting before shift between heating and cooling.
69 | SA Cool min air flow | 0-8200l/s
Supply air min. air flow setting for cooling.
70 | EA Cool min air flow | 0-8200l/s
Extract air min. air flow setting for cooling.
71 | Heating boost start limit | 0.00-40.00°C
Heating boost start temperature limit.
72 | Cooling boost start limit | 0.00-40.00°C
Cooling boost (comfort) start temperature limit.
73 | SA Filter alarm limit | 50-300Pa
Supply air filter pressure alarm limit setting.
74 | EA Filter alarm limit | 50-300Pa
Extract air filter pressure alarm limit setting.
75 | Int. Night heat room start temp | 5.00-25.00°C
Intermittent night heat function, extract air temperature setting for start.
76 | Int. Night heat room stop temp | 5.00-25.00°C
Intermittent night heat function, extract air temperature setting for stop.
77 | Int. Night heat SA temp setpoint | 5.00-40.00°C
Intermittent night heat function, supply air temperature setpoint during night heat.
78 | Int. Night heat SA airflow setpoint | 0-8200l/s
Intermittent night heat function, supply airflow setpoint during night heat.
79 | Int. Night heat EA airflow setpoint | 0-8200l/s
Intermittent night heat function, extract airflow setpoint during night heat.
80 | Summer night cool EA start temp | 17.00-27.00°C
Summer night cool function, extract air temperature setting for start.
81 | Summer night cool EA stop temp | 12.00-22.00°C
Summer night cool function, extract air temperature setting for stop.
82 | Summer night cool outdoor temp limit | 5.00-15.00°C
Summer night cool function, outdoor temperature limit.
83 | Summer night cool SA temp setpoint | 10.00-20.00°C
Summer night cool function, supply air temperature setpoint during summer night cool.
84 | Outdoor temp comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
85 | Outdoor temp comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
86 | Outdoor temp comp. Winter Y1. | 0.00-10.00°C
Level of winter compensation at X1.
87 | Outdoor temp comp. Summer X3. | 15.00-25.00°C
Startpoint of summer compensation.
88 | Outdoor temp comp. Summer X4. | 25.00-40.00°C
Endpoint of summer compensation.
89 | Outdoor temp comp. Summer Y2. | -10.00-10.00°C
Level of summer compensation at X4.
90 | Outdoor airflow comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
91 | Outdoor airflow comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
92 | Outdoor airflow comp. Winter Y1. | 0-50.00%
Level of airflow compensation at X1.
93 | Extra Reg. Sequence max output | 0-100.00%
Maximum output signal setting for the extra regulation sequence.
94 | EA/Room min temp alarm limit | 8.00-20.00°C
Setting for min extract air /room temp alarm no.40.
95 | SA Deviation alarm limit | 2.00-15.00°C
Setting for supply air temperature below present setpoint, alarm no.41.
96 | Reserve AV2
97 | SA Fan regulation mode | 0 - 3
Setting of regulation type for the supply air fan. 0=Airflow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan.
98 | EA Fan regulation mode | 0 - 3
Setting of regulation type for the extract air fan. 0=Airflow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan.
99 | ERS Step | 1 - 4
Setting of curve when temperature is above breakpoint.
100 | Temperature regulation mode. | 0 - 3
Setting of temperature regulation type. 0=ERS 1 reg. 1=ERS 2 reg. 2=SA reg. 3=EA/Room reg.
101 | Cooling off periode | 60 - 900s
Time setting for cooling off electrical heating coil.
102 | Cool step time set | 0 - 600s
Time setting between cool step shift.
103 | Cool restart time | 60 - 900s
Setting of time between two starts of the cool relays.
104 | Cool regulation mode | 0 - 6
Setting of cool regulation type 0=Controlled 0-10V 1=Controlled 10-0V 2=On/Off 1-step 3=On/Off 2-steps 4=On/Off 3-steps binary 5=CoolDX economi (PV 2.00) 6=CoolDX comfort (PV 3.00)
105 | Heating boost regulation mode. | 0 - 1
Setting for heating boost function. 0=Inactive. 1=Active.
106 | Cooling boost regulation mode. | 0 - 5
Setting of cooling boost regulation type. 0=Inactive. 1=Comfort. 2=Economy. 3=Sequence. 4=Comfort+economy (New in PV 5.00). 5=Economy+sequence (New in PV 5.00).
107 | Filter calibration mode | 0 - 5
Setting for required filter calibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter. 4=HX. 5=ReCO2 (New in PV 5.00).
108 | Air adjustment time, minutes | 0 - 1727
Setting for amount of minutes to air adjustment function.
109 | Air adjustment time, hours | 0 - 28
Setting for amount of hours to air adjustment function.
110 | Handterminal language | 0 - 18
0=Svenska 1=Norsk 2=Dansk 3=Suomi 4=English 5=Français 6=Deutsch 7=Polski 8=Český 9=Italiano 10=Español 11=Português 12=Pycckий 13=Eesti 14=Latviesu 15=Lietiviu 16=Nederlands 17=Magyar (New in PV 5.00) 18=Türkçe (New in PV 5.01)
111 | Summer night cool start, hour | 0-23
Setting for start time of summer night cooling function.
112 | Summer night cool start, minute | 0-59
Setting for start time of summer night cooling function.
113 | Summer night cool stop, hour | 0-23
Setting for stop time of summer night cooling function.
114 | Summer night cool stop, minute | 0-59
Setting for stop time of summer night cooling function.
115 | Extra regulation sequence cool mode | 0 - 2
Setting of extra regulation sequence cool type. 0=Inactive. 1=Comfort. 2=Economi.
116 | Extra regulation sequence heat mode | 0 - 2
Setting of extra regulation sequence heat type. 0=Inactive. 1=Comfort. 2=Economi.
117 | Morning boost time, hours | 0-23
Setting of morning boost time before normal operation.
118 | Morning boost time, minutes | 0-59
Setting of morning boost time before normal operation.
119 | Startup time | 0 - 600s
Setting of time for startup when the unit regulator is running with fixed signals.
120 | Start delay SA fan. | 0 - 600s
Setting of start delay time for the supply air fan.
121 | Start delay EA fan. | 0 - 600s
Setting of start delay time for the extract air fan after supply air fan has started.
122 | Air flow unit | 0 -2
Setting of air flow unit presented in the unit's handterminal and WEB. 0=l/s. 1=m3/s. 2=m3/h.
123 | Reserve AV3
124 | Year | 2000-2099
Setting for the unit's internal clock.
125 | Month | 1-12
Setting for the unit's internal clock.
126 | Date | 0-31
Setting for the unit's internal clock.
127 | Hour | 0-23
Setting for the unit's internal clock.
128 | Minute | 0-59
Setting for the unit's internal clock.
129 | Second | 0-59
Setting for the unit's internal clock.
130 | Time channel 1 status | 0-10,16-26
Low speed Högfart 0=Inactive 16=Inactive 1=Monday 17=Monday 2=Tuesday 18=Tuesday 3=Wednesday 19=Wednesday 4=Thursday. 20=Thursday 5=Friday 21=Friday 6=Saturday 22=Saturday 7=Sunday 23=Sunday 8=Monday..Friday 24=Monday..Friday 9=Monday..Sunday 25=Monday..Sunday 10=Saturday..Sunday 26=Saturday..Sunday
131 | Time channel 1 start hour | 0-23
132 | Time channel 1 start minute | 0-59
133 | Time channel 1 stop hour | 0-23
134 | Time channel 1 stop minute | 0-59
135 | Time channel 2 status | 0-10,16-26
136 | Time channel 2 start hour | 0-23
137 | Time channel 2 start minute | 0-59
138 | Time channel 2 stop hour | 0-23
139 | Time channel 2 stop minute | 0-59
140 | Time channel 3 status | 0-10,16-26
141 | Time channel 3 start hour | 0-23
142 | Time channel 3 start minute | 0-59
143 | Time channel 3 stop hour | 0-23
144 | Time channel 3 stop minute | 0-59
145 | Time channel 4 status | 0-10,16-26
146 | Time channel 4 start hour | 0-23
147 | Time channel 4 start minute | 0-59
148 | Time channel 4 stop hour | 0-23
149 | Time channel 4 stop minute | 0-59
150 | Time channel 5 status | 0-10,16-26
151 | Time channel 5 start hour | 0-23
152 | Time channel 5 start minute | 0-59
153 | Time channel 5 stop hour | 0-23
154 | Time channel 5 stop minute | 0-59
155 | Time channel 6 status | 0-10,16-26
156 | Time channel 6 start hour | 0-23
157 | Time channel 6 start minute | 0-59
158 | Time channel 6 stop hour | 0-23
159 | Time channel 6 stop minute | 0-59
160 | Time channel 7 status | 0-10,16-26
161 | Time channel 7 start hour | 0-23
162 | Time channel 7 start minute | 0-59
163 | Time channel 7 stop hour | 0-23
164 | Time channel 7 stop minute | 0-59
165 | Time channel 8 status | 0-10,16-26
166 | Time channel 8 start hour | 0-23
167 | Time channel 8 start minute | 0-59
168 | Time channel 8 stop hour | 0-23
169 | Time channel 8 stop minute | 0-59
170 | Extended low speed op. Hours set | 0-23
Setting for extended low speed operation.
171 | Extended low speed op. Minutes set | 0-59
Setting for extended low speed operation.
172 | Extended high speed op. Hours set | 0-23
Setting for extended low speed operation.
173 | Extended high speed op. Minutes set | 0-59
Setting for extended low speed operation.
174 | Communication operation mode | 0 - 4
Setting of unit operation mode from communication. 0=Auto operation. 1=Communication stop 1. 2=Communication low speed. 3=Communication high speed. 4=Communication stop 2 (New in PV 5.00). Summer night cool, intermittent night heat and morning boost functions works at stop 2.
175 | Service periode alarm. | 0-99
Setting for delay time in months before service alarm.
176 | External alarm 1 delay | 1 - 600s
Setting of delay time for external alarm no 1
177 | External alarm 2 delay | 1 - 600s
Setting of delay time for external alarm no 2
178 | Int. Night heat SA pressure setpoint | 20-750Pa
Intermittent night heat function, supply pressure setpoint during night heat.
179 | Int. Night heat EA pressure setpoint | 20-750Pa
Intermittent night heat function, extract pressure setpoint during night heat.
180 | Copy of Coil Status 1-16 | 0-65535
Bit 0=1x0001 Bit 1=1x0002 Bit 15=1x0016
181 | Copy of Coil Statust 17-32 | 0-65535
Bit 0=1x00017 Bit 1=1x00018 Bit 15=1x0032
182 | Copy of Coil Status 33-48 | 0-65535
Bit 0=1x00033 Bit 1=1x00034 Bit 15=1x0048
183 | Heat relay periodic func. | 0-3
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
184 | Cool relay 1 periodic func. | 0-3
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
185 | Cool relay 2 periodic func. | 0-3
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
186 | Slave control C-factor | 0.5 - 2.0
Slave regulator affection setting.
187 | SA dehumid P-band | 1.00 - 40.00
SA dehumid regulator P-band setting.
188 | SA dehumid C-factor | 0.000 - 2.500
SA dehumid regulator affection setting.
189 | Dewpoint reg. P-band | 1.00 - 40.00
Dewpoint regulator P-band setting.
190 | Dewpoint reg. C-factor | 0.000 - 2.500
Dewpoint regulator affection setting.
191 | AYC chilled water temperature set | 5.00-30.00°C
Setting of AYC chilled water temperature setpoint.
192 | Dewpoint neutralzone | 0.00-5.00°C
Dewpoint neutralzone setting.
193 | Comp. airflow | 0-30.00%
Setting of comp. airflow.
194 | Supply air-humidity | 10.00-90.00%
Setting of supply air-humidity.
195 | Water heating periodic op. time | 0-60min
Setting of periodic op. time (minute).
196 | Water heating interval | 0-168h
Setting of water heating interval time (hour).
197 | Cool periodic op. time | 0-60min
Setting of periodic op. time (minute).
198 | Cool interval | 0-168h
Setting of cool interval time (hour).
199 | P/C.HX. bypass adj. | -5.00-5.00°C
Setting of plate/coil heat exchange bypass adjustment.
200 | EA/Room temperature external func. | 0-3 | PV 5.15
Setting of EA/Room temperature (external) function. 0=Inactive. 1=Input signal on terminal 40..41. 2=Communication (AV 201). 3=Min/Max/Average (PV 5.15).
201 | EA/Room temperature com. | -55.00-125.00°C
Setting of EA/Room temperature via communication.
202 | Outdoor temperature external func. | 0-2
Setting of outdoor temperature (external) function. 0=Inactive. 1=Input signal on terminal 38..39. 2=Communication (AV 203).
203 | Outdoor temperature com. | -55.00-125.00°C
Setting of outdoor temperature via communication.
204 | Timeout temperature com. | 0-9999min
Setting of timeout for temperature via communication (AV 201, AV 203).
205 | Flow at fire function. | 0-3
Setting for activating the air fan operation at fire function 0=Inactive. 1=SA. 2=EA. 3=SA+EA.
206 | Air fan down regulation func. | 0-2
Setting for activating the air fan down regulation function 0=Inactive. 1=SA. 2=SA+EA.
207 | SA speed at fire. | 50.00-100.00%
Setting of supply air speed at fire.
208 | EA speed at fire. | 50.00-100.00%
Setting of extract air speed at fire.
209 | Temperature alarm setpoint. | -25.00-25.00°C
Temperature alarm function setting (no.80).
210 | Temperature alarm time. | 1-999s
Setting of delay time for temperature alarm (no.80).
211 | Supply air min P-band. | 1.00 - 40.00
Supply air min regulator P-band setting.
212 | Supply air min C-factor. | 0.000 - 2.500
Supply air min regulator affection setting.
213 | Supply air max P-band. | 1.00 - 40.00
Supply air max regulator P-band setting.
214 | Supply air max C-factor. | 0.000 - 2.500
Supply air max regulator affection setting.
215 | Year channel 1 function. | 0 - 3
0=Inactive. 1=Stop. 2=Low speed. 3=High speed.
216 | Year channel 1 start year. | 2000 - 2099
217 | Year channel 1 start month. | 1 - 12
218 | Year channel 1 start date. | 1 - 31
219 | Year channel 1 start hour. | 0 - 23
220 | Year channel 1 start minute. | 0 - 59
221 | Year channel 1 stop year. | 2000 - 2099
222 | Year channel 1 stop month. | 1 - 12
223 | Year channel 1 stop date. | 1 - 31
224 | Year channel 1 stop hour. | 0 - 23
225 | Year channel 1 stop minute. | 0 - 59
226 | Year channel 2 function. | 0 - 3
227 | Year channel 2 start year. | 2000 - 2099
228 | Year channel 2 start month. | 1 - 12
229 | Year channel 2 start date. | 1 - 31
230 | Year channel 2 start hour. | 0 - 23
231 | Year channel 2 start minute. | 0 - 59
232 | Year channel 2 stop year. | 2000 - 2099
233 | Year channel 2 stop month. | 1 - 12
234 | Year channel 2 stop date. | 1 - 31
235 | Year channel 2 stop hour. | 0 - 23
236 | Year channel 2 stop minute. | 0 - 59
237 | Year channel 3 function. | 0 - 3
238 | Year channel 3 start year. | 2000 - 2099
239 | Year channel 3 start month. | 1 - 12
240 | Year channel 3 start date. | 1 - 31
241 | Year channel 3 start hour. | 0 - 23
242 | Year channel 3 start minute. | 0 - 59
243 | Year channel 3 stop year. | 2000 - 2099
244 | Year channel 3 stop month. | 1 - 12
245 | Year channel 3 stop date. | 1 - 31
246 | Year channel 3 stop hour. | 0 - 23
247 | Year channel 3 stop minute. | 0 - 59
248 | Year channel 4 function. | 0 - 3
249 | Year channel 4 start year. | 2000 - 2099
250 | Year channel 4 start month. | 1 - 12
251 | Year channel 4 start date. | 1 - 31
252 | Year channel 4 start hour. | 0 - 23
253 | Year channel 4 start minute. | 0 - 59
254 | Year channel 4 stop year. | 2000 - 2099
255 | Year channel 4 stop month. | 1 - 12
256 | Year channel 4 stop date. | 1 - 31
257 | Year channel 4 stop hour. | 0 - 23
258 | Year channel 4 stop minute. | 0 - 59
259 | Year channel 5 function. | 0 - 3
260 | Year channel 5 start year. | 2000 - 2099
261 | Year channel 5 start month. | 1 - 12
262 | Year channel 5 start date. | 1 - 31
263 | Year channel 5 start hour. | 0 - 23
264 | Year channel 5 start minute. | 0 - 59
265 | Year channel 5 stop year. | 2000 - 2099
266 | Year channel 5 stop month. | 1 - 12
267 | Year channel 5 stop date. | 1 - 31
268 | Year channel 5 stop hour. | 0 - 23
269 | Year channel 5 stop minute. | 0 - 59
270 | Year channel 6 function. | 0 - 3
271 | Year channel 6 start year. | 2000 - 2099
272 | Year channel 6 start month. | 1 - 12
273 | Year channel 6 start date. | 1 - 31
274 | Year channel 6 start hour. | 0 - 23
275 | Year channel 6 start minute. | 0 - 59
276 | Year channel 6 stop year. | 2000 - 2099
277 | Year channel 6 stop month. | 1 - 12
278 | Year channel 6 stop date. | 1 - 31
279 | Year channel 6 stop hour. | 0 - 23
280 | Year channel 6 stop minute. | 0 - 59
281 | Year channel 7 function. | 0 - 3
282 | Year channel 7 start year. | 2000 - 2099
283 | Year channel 7 start month. | 1 - 12
284 | Year channel 7 start date. | 1 - 31
285 | Year channel 7 start hour. | 0 - 23
286 | Year channel 7 start minute. | 0 - 59
287 | Year channel 7 stop year. | 2000 - 2099
288 | Year channel 7 stop month. | 1 - 12
289 | Year channel 7 stop date. | 1 - 31
290 | Year channel 7 stop hour. | 0 - 23
291 | Year channel 7 stop minute. | 0 - 59
292 | Year channel 8 function. | 0 - 3
293 | Year channel 8 start year. | 2000 - 2099
294 | Year channel 8 start month. | 1 - 12
295 | Year channel 8 start date. | 1 - 31
296 | Year channel 8 start hour. | 0 - 23
297 | Year channel 8 start minute. | 0 - 59
298 | Year channel 8 stop year. | 2000 - 2099
299 | Year channel 8 stop month. | 1 - 12
300 | Year channel 8 stop date. | 1 - 31
301 | Year channel 8 stop hour. | 0 - 23
302 | Year channel 8 stop minute. | 0 - 59
303 | Filter select. | 0 - 3
Setting for filter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
304 | Prefilter select. | 0 - 3
Setting for prefilter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
305 | SA prefilter alarm limit. | 50-300Pa
Supply air prefilter pressure alarm limit setting.
306 | EA prefilter alarm limit. | 50-300Pa
Extract air prefilter pressure alarm limit setting.
307 | Prefilter calibration mode. | 0 - 3
Setting for requiered filtercalibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter.
308 | Xzone reheat function. | 0 - 4
Setting for Xzone reheat function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
309 | Xzone cooling function. | 0 - 5
Setting for Xzone cooling function. 0=Inactive. 1=0-10V. 2=10-0V. 3=On/off 1. 4=On/off 2. 5=On/off 3.
310 | Xzone temperature reg. Neutral zone. | 0.50-10.00°C
Xzone neutral zone setting before shift between heating and cooling.
311 | Xzone temperature regulation mode. | 0 - 3
Setting of Xzone temperature regulation type. 0=ERS 1 reg. 1=ERS 2 reg. 2=SA reg. 3=EA/Room reg.
312 | Xzone ERS Step. | 1 - 4
Setting of Xzone curve when temperature is above breakpoint.
313 | Xzone ERS 1 Diff. | 1.00 - 7.00°C
Supply air temperature difference setting accordning to the diagram for Xzone ERS 1.
314 | Xzone ERS 1 Breakpoint. | 12.00 - 26.00°C
Breakpoint setting accordning to the diagram for Xzone ERS 1.
315 | Xzone ERS 2 Breakpoint X1. | 10.00-38.00°C
Breakpoint X1 setting accordning to the diagram for Xzone ERS 2.
316 | Xzone ERS 2 Breakpoint Y1. | 10.00-40.00°C
Breakpoint Y1 setting accordning to the diagram for Xzone ERS 2.
317 | Xzone ERS 2 Breakpoint X2. | 11.00-39.00°C
Breakpoint X2 setting accordning to the diagram for Xzone ERS 2.
318 | Xzone ERS 2 Breakpoint Y2. | 10.00-40.00°C
Breakpoint Y2 setting accordning to the diagram for Xzone ERS 2.
319 | Xzone ERS 2 Breakpoint X3. | 12.00-40.00°C
Breakpoint X3 setting accordning to the diagram for Xzone ERS 2.
320 | Xzone ERS 2 Breakpoint Y3. | 10.00-40.00°C
Breakpoint Y3 setting accordning to the diagram for Xzone ERS 2.
321 | Xzone SA Temperature setpoint. | 10.00-40.00°C
Xzone supply air temperature setting, for supply air temp regulation mode.
322 | Xzone EA/Room Temperature setpoint. | 10.00-40.00°C
Xzone extract air/room temperature setting, for extract air/room temp regulation mode.
323 | Xzone SA Min temp setpoint. | 8.00-20.00°C
Xzone supply air min.setpoint during EA/room regulation mode.
324 | Xzone SA Max temp setpoint. | 16.00-50.00°C
Xzone supply air max.setpoint during EA/room regulation mode.
325 | Preheating function. | 0 - 4
Setting of preheating function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
326 | Preheating setpoint. | -30.00-30.00°C
Setting of preheating temperature setpoint.
327 | Xzone P-band. | 1.00-40.00
Xzone regulator P-band setting.
328 | Xzone SA reheat C-factor. | 0.000 - 2.500
Xzone supply air reheat regulator affection setting.
329 | Xzone SA cooling C-factor. | 0.000 - 2.500
Xzone supply air cooling regulator affection setting.
330 | Xzone EA reheat C-factor. | 0.000 - 2.500
Xzone extract air reheat regulator affection setting.
331 | Xzone EA cooling C-factor. | 0.000 - 2.500
Xzone extract air cooling regulator affection setting.
332 | Xzone SA min P-band. | 1.00 - 40.00
Xzone supply air min regulator P-band setting.
333 | Xzone SA min C-factor. | 0.000 - 2.500
Xzone supply air min regulator affection setting.
334 | Xzone SA max P-band. | 1.00 - 40.00
Xzone supply air max regulator P-band setting.
335 | Xzone SA max C-factor. | 0.000 - 2.500
Xzone supply air min regulator affection setting.
336 | Preheat P-band. | 1.00 - 40.00
Preheat regulator P-band setting.
337 | Preheat C-factor. | 0.000 - 2.500
Preheat regulator affection setting.
338 | ReCO2 CO2 function. | 0 - 2
Setting of ReCO2 CO2 function. 0=Inactive. 1=CO2. 2=CO2+flow.
339 | ReCO2 CO2 setpoint. | 0-100.00%
Setting of ReCO2 CO2 setpoint.
340 | ReCO2 cooling function. | 0 - 2
Setting of ReCO2 cooling function. 0=Inactive. 1=Comfort. 2=Economy.
341 | ReCO2 heating function. | 0 - 2
Setting of ReCO2 heating function. 0=Inactive. 1=Comfort. 2=Economy.
342 | ReCO2 min outdoor air. | 0-8200l/s
Setting of ReCO2 min outdoor air.
343 | ReCO2 min exhaust air. | 0-8200l/s
Setting of ReCO2 min exhaust air.
344 | ReCO2 CO2 P-band. | 1.00 - 100.00
ReCO2 CO2 regulator P-band setting.
345 | ReCO2 CO2 C-factor. | 0.000 - 5.000
ReCO2 CO2 regulator affection setting.
346 | ReCO2 CO2 flow C-factor. | 0.000 - 5.000
ReCO2 flow regulator affection setting.
347 | ReCO2 heating C-factor. | 0.000 - 5.000
ReCO2 heating regulator affection setting.
348 | ReCO2 cooling C-factor. | 0.000 - 5.000
ReCO2 cooling regulator affection setting.
349 | AYC function. | 0 - 3
Setting of AYC function. 0=Inactive. 1=Cool. 2=Heat. 3=Cool+heat.
350 | AYC heat temp set. | 10.00-80.00°C
Setting of AYC heated water temperature setpoint.
351 | AYC night comp. channel. | 1 - 2
Setting of AYC night compensation channel. 1=Channel 1. 2=Channel 2.
352 | AYC channel start hour. | 0-23h
Setting of AYC channel start time (hour).
353 | AYC channel start minute. | 0-59min
Setting of AYC channel start time (minute).
354 | AYC channel stop hour. | 0-23h
Setting of AYC channel stop time (hour).
355 | AYC channel stop minute. | 0-59min
Setting of AYC channel stop time (minute).
356 | AYC channel period. | 0-10
Setting of AYC channel period. 0=Inactive 1=Monday 2=Tuesday 3=Wednesday 4=Thursday 5=Friday 6=Saturday 7=Sunday 8=Monday..Friday 9=Monday..Sunday 10=Saturday..Sunday
357 | AYC heat P-band. | 1.00 - 40.00
AYC heat regulator P-band setting.
358 | AYC heat C-factor. | 0.000 - 2.500
AYC heat regulator affection setting.
359 | AYC cool P-band. | 1.00 - 40.00
AYC cool regulator P-band setting.
360 | AYC cool C-factor. | 0.000 - 2.500
AYC cool regulator affection setting.
361 | AYC heat out comp. X1. | -40.00-40.00°C
AYC outdoor compensation of heated water, outdoor temp X1 setting.
362 | AYC heat out comp. Y1. | 10.00-80.00°C
AYC outdoor compensation of heated water, heated water temp Y1 setting.
363 | AYC heat out comp. X2. | -40.00-40.00°C
AYC outdoor compensation of heated water, outdoor temp X2 setting.
364 | AYC heat out comp. Y2. | 10.00-80.00°C
AYC outdoor compensation of heated water, heated water temp Y2 setting.
365 | AYC heat out comp. X3. | -40.00-40.00°C
AYC outdoor compensation of heated water, outdoor temp X3 setting.
366 | AYC heat out comp. Y3. | 10.00-80.00°C
AYC outdoor compensation of heated water, heated water temp Y3 setting.
367 | AYC heat room comp. temp limit. | 0.00-40.00°C
AYC room compensation of heated water, heated water temp limit setting.
368 | AYC heat room comp P-band. | 1.00-10.00°C
AYC room compensation of heated water, heated water P-band setting.
369 | AYC heat night comp temp. | -10.00-10.00°C
AYC night compensation of heated water, heated water night setting.
370 | AYC heat pump on temp. | -40.00-40.00°C
AYC pump operation of heated water, outdoor temp start setting.
371 | AYC heat pump off temp. | -40.00-40.00°C
AYC pump operation of heated water, outdoor temp stop setting.
372 | AYC heat pump alarm. | 0 - 3
Setting for selecting the AYC heated water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
373 | AYC heat per op function. | 0 - 3
Setting for selecting the AYC heated water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
374 | AYC heat per op time. | 0-60min
AYC periodic operation of heated water, time (minute) setting.
375 | AYC heat per op interval. | 0-168h
AYC periodic operation of heated water, interval time (hour) setting.
376 | AYC cool out comp. X1. | -40.00-40.00°C
AYC outdoor compensation of chilled water, outdoor temp X1 setting.
377 | AYC cool out comp. Y1. | 10.00-80.00°C
AYC outdoor compensation of chilled water, chilled water temp Y1 setting.
378 | AYC cool out comp. X2. | -40.00-40.00°C
AYC outdoor compensation of chilled water, outdoor temp X2 setting.
379 | AYC cool out comp. Y2. | 10.00-80.00°C
AYC outdoor compensation of chilled water, chilled water temp Y2 setting.
380 | AYC cool out comp. X3. | -40.00-40.00°C
AYC outdoor compensation of chilled water, outdoor temp X3 setting.
381 | AYC cool out comp. Y3. | 10.00-80.00°C
AYC outdoor compensation of chilled water, chilled water temp Y3 setting.
382 | AYC cool room comp. temp limit. | 0.00-40.00°C
AYC room compensation of chilled water, chilled water temp limit setting.
383 | AYC cool room comp. P-band. | 1.00-10.00°C
AYC room compensation of chilled water, chilled water P-band setting.
384 | AYC cool night comp temp. | -10.00-10.00°C
AYC night compensation of chilled water, chilled water night setting.
385 | AYC cool pump on temp. | -40.00-40.00°C
AYC pump operation of chilled water, outdoor temp start setting.
386 | AYC cool pump off temp. | -40.00-40.00°C
AYC pump operation of chilled water, outdoor temp stop setting.
387 | AYC cool pump alarm. | 0 - 3
Setting for selecting the AYC chilled water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
388 | AYC cool per op function. | 0 - 3
Setting for selecting the AYC chilled water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
389 | AYC cool per op time. | 0-60min
AYC periodic operation of chilled water, time (minute) setting.
390 | AYC cool per op interval. | 0-168h
AYC periodic operation of chilled water, interval time (hour) setting.
391 | IO-mod 3 output 1 function. | 0 - 10
Setting of I/O-module no. 3 relay 1 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
392 | IO-mod 3 output 2 function. | 0 - 10
Setting of I/O-module no. 3 relay 2 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
393 | Humid reg. func. | 0 - 2 | PV 5.10
Setting for selecting humidifying function. 0=Inactive. 1=Supply air. 2=Extract air.
394 | Humid reg. Start. | 10.00-90.00% | PV 5.10
Humidifying start limit setting.
395 | Humid reg. Stop. | 15.00-95.00% | PV 5.10
Humidifying stop limit setting.
396 | Min/Max/Average SensNumber | 1 - 4 | PV 5.15
Setting for selecting numbers of sensors to the Min/Max/Average function.
397 | Min/Max/Average SensFunction | 0 - 2 | PV 5.15
Setting for selecting sensor function. 0=Min. 1=Max. 2=Average.

## Binary Inputs
GB.BACnet480.100915
Binary Inputs (RO).
Object Instance | Object Name | Min/Max | Misc
0 | Heat output | 0-1
Status for relay output.
1 | Cool output 1 | 0-1
Status for relay output.
2 | Cool output 2 | 0-1
Status for relay output.
3 | Low speed output | 0-1
Status for relay output.
4 | High speed output | 0-1
Status for relay output.
5 | A-alarm. | 0-1
Status for relay output.
6 | B-alarm. | 0-1
Status for relay output.
7 | Operation output | 0-1
Status for relay output.
8 | Damper output | 0-1
Status for relay output.
9 | External low speed input | 0-1
Status for digital input.
10 | External high speed input | 0-1
Status for digital input.
11 | External alarm 1 input | 0-1
Status for digital input.
12 | External alarm 2 input | 0-1
Status for digital input.
13 | External fire alarm input. | 0-1
Status for digital input.
14 | External stop input | 0-1
Status for digital input.
15 | DIP Switch 1 | 0-1
Status for dip switch setting.
16 | DIP Switch 2 | 0-1
Status for dip switch setting.
17 | DIP Switch 3 | 0-1
Status for dip switch setting.
18 | DIP Switch 4 | 0-1
Status for dip switch setting.
19 | DIP Switch 5 | 0-1
Status for dip switch setting.
20 | DIP Switch 6 | 0-1
Status for dip switch setting.
21 | AYC heat pump output | 0-1
Status for AYC heat pump output.
22 | AYC cool pump output | 0-1
Status for AYC cool pump output.
23 | C.HX. pump output | 0-1
Status for coil heat exchanger pump output.
24 | R.HX rotation monitor | 0-1
Status from the rotation detector.
25 | Xzone heat output | 0-1
Status for relay output.
26 | Xzone cool output 1 | 0-1
Status for relay output.
27 | Xzone cool output 2 | 0-1
Status for relay output.
28 | Pre-heat output | 0-1
Status for relay output.
29 | IO-mod 3 output 1 | 0-1
Status for I/O-module no. 3 relay 1 output.
30 | IO-mod 3 output 2 | 0-1
Status for I/O-module no. 3 relay 2 output.
31 | IO-mod 4 output 1 | 0-1 | PV 5.10
Status for I/O-module no. 4 relay 1 output.
32 | Reserve BI12
33 | Reserve BI13
34 | Reserve BI14
35 | Reserve BI15
36 | Reserve BI16
37 | Reserve BI17
38 | Reserve BI18
39 | Reserve BI19
40 | Reserve BI20
41 | Reserve BI21
42 | Reserve BI22
43 | Reserve BI23
44 | Reserve BI24
45 | Reserve BI25
46 | Reserve BI26
47 | Reserve BI27
48 | Alarm number 1 | 0-1
Status if alarm number 1 is active.
49 | Alarm number 2 | 0-1
Status if alarm number 2 is active.
50 | Alarm number 3 | 0-1
Status if alarm number 3 is active.
247 | Alarm number 200 | 0-1
Status if alarm number 200 is active.
248 | Info number 1 | 0-1
Status if info number 1 is active.
249 | Info number 2 | 0-1
Status if info number 2 is active.
250 | Info number 3 | 0-1
Status if info number 3 is active.
347 | Info number 100 | 0-1
Status if info number 100 is active.

## Binary Value
GB.BACnet480.100915
Binary Value (R/W).
Object Instance | Object Name | Min/Max | Misc
0 | Alarm reset | 0-1
Resets tripped alarms.
1 | SA Boosting func. | 0-1
Setting for activating the boost function for the supply air fan.
2 | EA Boosting func. | 0-1
Setting for activating the boost function for the extract air fan.
3 | R.HX. Defrost func. | 0-1
Setting for activating the defrost function for the rotary heat exchanger.
4 | SA Down regulation func. | 0-1
Setting for activating the down regulation function for the supply air fan. (Moved to AV 206 in PV 3.00)
5 | Reserve BV1
6 | Reserve BV2
7 | Cool operation mode | 0-1
Setting for cooling between off and auto operation.
8 | Int. Night heat func. | 0-1
Setting for activating the intermittent night heat function.
9 | Damper func. | 0-1
Setting for activating the damper output relay during int. night heat.
10 | Summer night cooling | 0-1
Setting for activating the suumer night cool function.
11 | Temp displacement | 0-1
Setting for activating the external temperature displacement function.
12 | Outdoor temp compensation | 0-1
Setting for activating the outdoor temperature compensation function.
13 | Outdoor airflow compensation | 0-1
Setting for activating the outdoor airflow compensation function.
14 | Auto. Summer/winter switch | 0-1
Setting for activating the automatic switch between summer/winter time function.
15 | Switch clock func. | 0-1
Setting for switch clock function type. 0=Stop - low speed - high speed. 1=Low speed - high speed.
16 | Internal fire alarm func. | 0-1
Setting for activating the internal fire alarm function.
17 | EA at fire | 0-1
Setting for activating the extract air fan operation at fire function. (Moved to 4x0206 in PV 3.00)
18 | External alarm 1 active at closure | 0-1
Setting for external alarm number 1 condition to be activated. 0=Alarm at closed input. 1=Alarm at open input.
19 | External alarm 2 active at closure | 0-1
Setting for external alarm number 2 condition to be activated. 0=Alarm at closed input. 1=Alarm at open input.
20 | Reserve BV3
21 | Dewpoint reg. func. | 0-1
Setting for activating the dewpoint regulator funktion.
22 | Dehumid reg. func. | 0-1
Setting for activating the dehumid regulator funktion.
23 | External fire alarm func. | 0-1
Setting for external fire resetting function. 0=Manual. 1=Automatic.
24 | External alarm 1 func. | 0-1
Setting for external alarm 1 resetting function. 0=Manual. 1=Automatic.
25 | External alarm 2 func. | 0-1
Setting for external alarm 2 resetting function. 0=Manual. 1=Automatic.
26 | Temperature alarm func. | 0-1
Setting for activating temperature below setpoint alarm function (no.80).
27 | Int. Night heat output func. | 0-1
Setting for selecting the intermittent night heat output function. 0=IQnomic 1=IQnomic+
28 | AYC heat out comp. func. | 0-1
Setting for selecting the AYC outdoor comp. heated water function. 0=Inactive 1=Active
29 | AYC heat room comp. func. | 0-1
Setting for selecting the AYC room comp. heated water function. 0=Inactive 1=Active
30 | AYC heat room comp. night block func. | 0-1
Setting for selecting the AYC room comp. heated water night block function. 0=Inactive 1=Active
31 | AYC heat night comp. func. | 0-1
Setting for selecting the AYC night comp. heated water function. 0=Inactive 1=Active
32 | AYC heat valve signal func. | 0-1
Setting for selecting the AYC valve signal heated water alarm function. 0=Inactive 1=Active
33 | AYC cool out comp. func. | 0-1
Setting for selecting the AYC outdoor comp. chilled water function. 0=Inactive 1=Active
34 | AYC cool room comp. func. | 0-1
Setting for selecting the AYC room comp. chilled water function. 0=Inactive 1=Active
35 | AYC cool room comp. night block func. | 0-1
Setting for selecting the AYC room comp. chilled water night block function. 0=Inactive 1=Active
36 | AYC cool night comp. func. | 0-1
Setting for selecting the AYC night comp. chilled water function. 0=Inactive 1=Active
37 | AYC cool valve signal func. | 0-1
Setting for selecting the AYC valve signal chilled water alarm function. 0=Inactive 1=Active
38 | Reserve BV4

## Notification Class
GB.BACnet480.100915
Notification Class.
Object Instance | Object Name | Min/Max | Misc
0 | NC 00 A-Alarm |  | PV 5.15
Notification class for A-Alarm.
1 | NC 00 B-Alarm |  | PV 5.15
Notification class for B-Alarm.